## Sheet1
Date/Time | Base simulated: avg tmp c | Config 1 uniform prior simulated: avg tmp C | Config 1 normal prior simulated: avg tmp C | Config 2 normal prior simulated: avg tmp C | Config 2 uni prior simulated: avg tmp C | Config 3 uni prior simulated: avg tmp C | measured: avg tmp c | Base simulated: heating energy kwh | Config 1 uniform prior simulated: heating energy kWh | Config 1 normal prior simulated: heating energy kWh | Config 2 normal prior simulated: heating energy kWh | Config 2 uniform prior simulated: heating energy kWh | Config 3 uniform prior simulated: heating energy kWh | measured: heating energy kwh |  | Base daily simulated | Config 2 normal prior simulated daily heating energy kWh | Config 2 uni prior simulated daily heating energy kWh | daily measured | [9 empty] | tmp diff sqr | avg sqrt | ht egy diff sqr | avg sqrt | ht daily diff sqr | avg sqrt | ht egy diff sqr config 1 uni prior | avg sqrt | ht egy diff sqr config 1 normal prior | avg sqrt | ht egy diff sqr config 2 normal prior |  | ht egy diff sqr config 2 uni prior |  | ht egy diff sqr config 3 uni prior
[8 empty] | 44380.6763 | 33654.6388 | 36106.6288 | 43840.7561 | 45207.045 | 41251.9731 | 43437.0475 | [6 empty] | hourly tmp | hourly heat energy | Config 1 uni prior hourly heating | Config 1 normal prior hourly heating | Config 2 normal prior hourly heating | Config 2 uni prior hourly heating | Config 3 uni prior hourly heating | daily heating
01/01 01:00:00 | 22.8836 | 24.0225 | 22.8207 | 23.1205 | 23.5268 | 23.7774 | 21.2789 | 14.4148 | 12.8016 | 10.3698 | 15.2258 | 17.0452 | 15.1498 | 24.5461 | 2017-01-01 | 588.0771 | 621.0393 | 586.4208 | 560.902 | mbe | -0.016406 | -0.021724 | [6 empty] | 2.5751 | 1.4546 | 102.6428 | 16.4618 | 738.4898 | 85.694 | 137.9322 | 16.2962 | 200.967 | 16.4 | 86.8683 | 15.9762 | 56.2625 | 15.589 | 88.291 | 15.6803
01/01 02:00:00 | 22.6793 | 23.7783 | 22.6239 | 22.86 | 23.251 | 23.5093 | 21.2374 | 14.1142 | 10.6962 | 10.2046 | 14.6307 | 16.4213 | 14.5693 | 24.6216 | 2017-01-02 | 544.1777 | 569.3812 | 576.6761 | 549.1573 | cvrmse | 0.066421 | 0.8186 | 0.81037 | 0.81553 | 0.79445 | 0.7752 | 0.77974 | 0.17755 | 2.0791 |  | 110.4037 |  | 24.7962 |  | 193.9152 |  | 207.8482 |  | 99.8172 |  | 67.2435 |  | 101.0484
01/01 03:00:00 | 22.5477 | 23.5984 | 22.4905 | 22.6283 | 23.0223 | 23.2701 | 21.1424 | 13.5023 | 10.5622 | 9.8582 | 13.9262 | 15.6058 | 13.8675 | 25.9272 | 2017-01-03 | 594.4308 | 542.2999 | 632.4145 | 490.4736 | [9 empty] | 1.9749 |  | 154.3794 |  | 10807.1031 |  | 236.0833 |  | 258.2138 |  | 144.0236 |  | 106.5306 |  | 145.4369
01/01 04:00:00 | 22.4106 | 23.4677 | 22.3592 | 22.4009 | 22.7912 | 23.0345 | 21.0858 | 13.3047 | 11.9511 | 9.7111 | 13.6169 | 15.1902 | 13.5677 | 25.2162 | 2017-01-04 | 742.5696 | 662.0426 | 665.7557 | 673.9141 | [9 empty] | 1.7552 |  | 141.8835 |  | 4713.5716 |  | 175.9645 |  | 240.41 |  | 134.5444 |  | 100.5205 |  | 135.6872
01/01 05:00:00 | 22.2547 | 23.2601 | 22.2075 | 22.1495 | 22.5265 | 22.7744 | 21.0681 | 12.971 | 11.3615 | 9.5236 | 13.2239 | 14.7316 | 13.1833 | 25.7837 | 2017-01-05 | 1067.122 | 1061.6052 | 1059.8638 | 994.3177 | [9 empty] | 1.408 |  | 164.1654 |  | 5300.4724 |  | 208.0003 |  | 264.391 |  | 157.7488 |  | 122.1501 |  | 158.7712
01/01 06:00:00 | 22.0888 | 22.982 | 22.0461 | 21.8824 | 22.2415 | 22.4998 | 21.0055 | 12.8076 | 11.0787 | 9.4162 | 12.9547 | 14.4323 | 12.9138 | 26.09 | 2017-01-06 | 1107.4632 | 1069.6262 | 1091.8957 | 1041.1751 | [9 empty] | 1.1735 |  | 176.4221 |  | 4394.1131 |  | 225.3391 |  | 278.0167 |  | 172.5378 |  | 135.9028 |  | 173.6134
01/01 07:00:00 | 21.9106 | 22.6989 | 21.8725 | 21.5943 | 21.9396 | 22.2029 | 20.964 | 12.6571 | 10.8386 | 9.3246 | 12.7573 | 14.1648 | 12.7235 | 26.8461 | 2017-01-07 | 1137.6961 | 1154.0907 | 1162.5453 | 1137.1947 | [9 empty] | 0.89609 |  | 201.3285 |  | 0.25144 |  | 256.2399 |  | 307.0024 |  | 198.4936 |  | 160.8155 |  | 199.4481
01/01 08:00:00 | 21.7213 | 22.4117 | 21.6897 | 21.3015 | 21.6273 | 21.8999 | 20.9107 | 12.3725 | 10.6148 | 9.1728 | 12.4439 | 13.7853 | 12.4266 | 26.4791 | 2017-01-08 | 1186.4469 | 1160.9133 | 1166.2347 | 1255.9181 | [9 empty] | 0.65705 |  | 198.9963 |  | 4826.2455 |  | 251.6783 |  | 299.5104 |  | 196.9882 |  | 161.1341 |  | 197.4727
01/01 09:00:00 | 21.5247 | 22.1222 | 21.4983 | 21.0034 | 21.3071 | 21.5977 | 21.2849 | 14.9814 | 14.4695 | 33.4693 | 39.4508 | 43.2283 | 40.6266 | 79.093 | 2017-01-09 | 1123.9497 | 1084.1866 | 1089.1597 | 1116.6505 | [9 empty] | 0.057524 |  | 4110.2886 |  | 53.2792 |  | 4176.191 |  | 2081.5206 |  | 1571.5028 |  | 1286.2751 |  | 1479.6641
01/01 10:00:00 | 21.3161 | 21.8283 | 21.3915 | 20.8671 | 21.1631 | 21.4655 | 22.5181 | 25.4785 | 18.1273 | 49.7071 | 58.7246 | 61.1289 | 59.5478 | 45.3773 | 2017-01-10 | 865.2307 | 846.2467 | 833.266 | 850.9266 | [9 empty] | 1.4448 |  | 395.961 |  | 204.6063 |  | 742.5647 |  | 18.7472 |  | 178.1509 |  | 248.1139 |  | 200.8038
01/01 11:00:00 | 21.2402 | 21.684 | 21.7875 | 21.6492 | 22.1328 | 22.3326 | 23.2836 | 48.2223 | 40.6262 | 42.2777 | 55.6346 | 45.9705 | 45.4801 | 5.0549 | 2017-01-11 | 400.3141 | 381.3221 | 432.632 | 483.1687 | [9 empty] | 4.1755 |  | 1863.4217 |  | 6864.8765 |  | 1265.312 |  | 1385.5356 |  | 2558.3026 |  | 1674.0821 |  | 1634.1914
01/01 12:00:00 | 21.5065 | 21.8223 | 22.626 | 23.0606 | 23.5127 | 23.7401 | 23.3112 | 49.1908 | 37.8058 | 34.6907 | 42.0091 | 35.7935 | 34.9264 | 11.0444 | 2017-01-12 | 62.1191 | 52.3078 | 62.9055 | 117.9474 | [9 empty] | 3.2569 |  | 1455.1435 |  | 3116.8008 |  | 716.1722 |  | 559.1467 |  | 958.8131 |  | 612.5152 |  | 570.3486
01/01 13:00:00 | 22.8177 | 23.5373 | 23.6949 | 24.5218 | 24.3978 | 24.7399 | 23.3196 | 41.0861 | 27.9029 | 31.559 | 37.1072 | 32.7678 | 32.0991 | 7.5984 | 2017-01-13 | 675.3123 | 676.3413 | 695.6537 | 619.4299 | [9 empty] | 0.25193 |  | 1121.4274 |  | 3122.8323 |  | 412.2723 |  | 574.1072 |  | 870.7682 |  | 633.4994 |  | 600.2833
01/01 14:00:00 | 23.9038 | 24.7077 | 24.2943 | 25.1022 | 24.7904 | 25.2146 | 23.2855 | 37.8687 | 25.364 | 29.7493 | 35.5202 | 31.2844 | 30.5271 | 15.6899 | 2017-01-14 | 734.7578 | 676.3281 | 687.9446 | 694.0954 | [9 empty] | 0.38226 |  | 491.9026 |  | 1653.4323 |  | 93.5896 |  | 197.668 |  | 393.241 |  | 243.189 |  | 220.1425
01/01 15:00:00 | 24.2003 | 25.0223 | 24.5544 | 25.2716 | 24.968 | 25.4173 | 23.3007 | 35.4855 | 23.9371 | 27.7943 | 32.9814 | 29.0308 | 28.2678 | 9.554 | 2017-01-15 | 683.5038 | 699.4366 | 712.3262 | 636.3927 | [9 empty] | 0.80931 |  | 672.4439 |  | 2219.4555 |  | 206.8754 |  | 332.7098 |  | 548.8447 |  | 379.3469 |  | 350.2064
01/01 16:00:00 | 24.3384 | 25.2092 | 24.7457 | 25.4097 | 25.1041 | 25.5778 | 23.2139 | 32.9364 | 22.3441 | 25.8198 | 30.4201 | 26.8673 | 25.9972 | 14.6445 | 2017-01-16 | 672.5091 | 720.9061 | 724.2368 | 666.7662 | [9 empty] | 1.2647 |  | 334.5908 |  | 32.9812 |  | 59.2838 |  | 124.8869 |  | 248.8674 |  | 149.3953 |  | 128.8826
01/01 17:00:00 | 24.4369 | 25.3521 | 24.8994 | 25.5465 | 25.2178 | 25.7069 | 23.0397 | 31.1565 | 20.9061 | 24.3197 | 28.3481 | 25.0431 | 24.1527 | 17.0593 | 2017-01-17 | 180.4849 | 195.3284 | 199.0928 | 269.6928 | [9 empty] | 1.9522 |  | 198.7333 |  | 7958.0546 |  | 14.7985 |  | 52.7144 |  | 127.437 |  | 63.7417 |  | 50.3167
01/01 18:00:00 | 24.5602 | 25.546 | 25.0883 | 25.6643 | 25.3418 | 25.8311 | 22.66 | 30.7904 | 20.6124 | 24.014 | 28.8232 | 24.9833 | 24.8407 | 21.3629 | 2017-01-18 | 433.8549 | 433.6902 | 434.0727 | 485.267 | [9 empty] | 3.6108 |  | 88.8773 |  | 2643.2051 |  | 0.56319 |  | 7.0284 |  | 55.6562 |  | 13.1077 |  | 12.095
01/01 19:00:00 | 24.5172 | 25.5456 | 25.0903 | 25.5601 | 25.2318 | 25.6942 | 22.6984 | 29.4039 | 20.0698 | 23.1098 | 27.3444 | 23.8843 | 23.7745 | 38.0397 | 2017-01-19 | 640.1616 | 536.3148 | 605.4189 | 497.6174 | [9 empty] | 3.3079 |  | 74.5771 |  | 20318.8589 |  | 322.92 |  | 222.9031 |  | 114.3907 |  | 200.3754 |  | 203.498
01/01 20:00:00 | 24.3376 | 25.3003 | 24.9103 | 25.3105 | 24.9034 | 25.4071 | 22.6404 | 23.3649 | 15.0467 | 17.5637 | 21.1474 | 18.6134 | 18.5502 | 8.6487 | 2017-01-20 | 339.5382 | 348.2764 | 347.3709 | 387.7396 | [9 empty] | 2.8805 |  | 216.5666 |  | 2323.3765 |  | 40.9339 |  | 79.4767 |  | 156.2172 |  | 99.2962 |  | 98.039
01/01 21:00:00 | 24.1469 | 25.0433 | 24.7237 | 25.0323 | 24.5407 | 25.0676 | 22.1426 | 22.0332 | 14.5891 | 16.783 | 19.9891 | 17.7047 | 17.6052 | 18.5203 | 2017-01-21 | 173.6274 | 181.218 | 187.3689 | 172.228 | [9 empty] | 4.0169 |  | 12.3405 |  | 1.9582 |  | 15.4543 |  | 3.0183 |  | 2.1574 |  | 0.66518 |  | 0.83746
01/01 22:00:00 | 23.9594 | 24.7864 | 24.5518 | 24.7129 | 24.154 | 24.704 | 21.847 | 20.6901 | 14.0551 | 15.9544 | 18.8318 | 16.7099 | 16.6332 | 20.1035 | 2017-01-22 | 125.3005 | 139.7485 | 186.8034 | 124.9263 | [9 empty] | 4.4624 |  | 0.34409 |  | 0.14008 |  | 36.583 |  | 17.2149 |  | 1.6171 |  | 11.5164 |  | 12.0429
01/01 23:00:00 | 23.7556 | 24.5057 | 24.3592 | 24.3228 | 23.7592 | 24.385 | 21.6708 | 19.9532 | 13.6227 | 15.427 | 18.2437 | 16.2411 | 16.1361 | 21.9814 | 2017-01-23 | 523.0036 | 484.7812 | 455.3555 | 514.5743 | [9 empty] | 4.3464 |  | 4.1136 |  | 71.053 |  | 69.8665 |  | 42.9592 |  | 13.9704 |  | 32.9503 |  | 34.1668
01/01 24:00:00 | 23.5285 | 24.2044 | 24.1455 | 23.9944 | 23.4196 | 24.0516 | 21.5283 | 19.2909 | 13.2361 | 14.9611 | 17.6843 | 15.7927 | 15.6776 | 21.6197 | 2017-01-24 | 565.2455 | 577.0012 | 633.3373 | 599.3178 | [9 empty] | 4.0008 |  | 5.4236 |  | 1160.9166 |  | 70.2853 |  | 44.3371 |  | 15.4875 |  | 33.954 |  | 35.3086
01/02 01:00:00 | 23.2904 | 23.9507 | 23.9161 | 23.6606 | 23.073 | 23.7703 | 21.4291 | 19.6903 | 13.0979 | 15.0433 | 18.1199 | 16.2572 | 16.1547 | 22.4379 | 2017-01-25 | 316.9051 | 352.758 | 362.9622 | 420.8909 | [9 empty] | 3.4646 |  | 7.5491 |  | 10813.0466 |  | 87.235 |  | 54.6806 |  | 18.6449 |  | 38.2008 |  | 39.4785
01/02 02:00:00 | 23.0302 | 23.6544 | 23.6647 | 23.3 | 22.6972 | 23.4358 | 21.3725 | 16.2003 | 12.834 | 14.638 | 17.5363 | 15.7838 | 15.6808 | 23.4368 | 2017-01-26 | 573.5358 | 517.2604 | 559.8651 | 611.6458 | [9 empty] | 2.7481 |  | 52.3667 |  | 1452.3684 |  | 112.4189 |  | 77.4194 |  | 34.8156 |  | 58.5681 |  | 60.1548
01/02 03:00:00 | 22.8064 | 23.3654 | 23.4138 | 23.008 | 22.3919 | 23.1143 | 21.2686 | 15.8635 | 12.4449 | 14.1897 | 16.9806 | 15.3206 | 15.2072 | 24.4167 | 2017-01-27 | 737.7099 | 754.6852 | 717.2707 | 823.8809 | [9 empty] | 2.3647 |  | 73.1581 |  | 7425.4483 |  | 143.3251 |  | 104.592 |  | 55.2956 |  | 82.7396 |  | 84.8155
01/02 04:00:00 | 22.6381 | 23.11 | 23.1685 | 22.737 | 22.1086 | 22.8278 | 21.2266 | 15.0912 | 12.0472 | 13.5368 | 16.0724 | 14.5098 | 14.4034 | 23.8576 | 2017-01-28 | 860.8959 | 796.7179 | 841.9169 | 830.5587 | [9 empty] | 1.9923 |  | 76.8496 |  | 920.3447 |  | 139.4853 |  | 106.5187 |  | 60.6091 |  | 87.3818 |  | 89.3828
01/02 05:00:00 | 22.4656 | 22.8541 | 22.9239 | 22.4628 | 21.8211 | 22.5432 | 21.2062 | 14.5627 | 11.6055 | 13.0441 | 15.4051 | 13.9351 | 13.8365 | 24.1167 | 2017-01-29 | 843.9499 | 826.594 | 880.0603 | 761.4316 | [9 empty] | 1.5862 |  | 91.2778 |  | 6809.2593 |  | 156.5285 |  | 122.602 |  | 75.8919 |  | 103.6651 |  | 105.6808
01/02 06:00:00 | 22.2902 | 22.5863 | 22.6852 | 22.1874 | 21.5319 | 22.2621 | 21.2125 | 14.3469 | 9.8006 | 10.8676 | 15.0136 | 13.6213 | 12.3436 | 24.6332 | 2017-01-30 | 738.0459 | 807.1026 | 807.8738 | 891.2322 | [9 empty] | 1.1616 |  | 105.8075 |  | 23466.0584 |  | 220.0053 |  | 189.492 |  | 92.537 |  | 121.2625 |  | 151.034
01/02 07:00:00 | 22.1231 | 22.387 | 22.5031 | 21.9284 | 21.2622 | 22.0455 | 21.2311 | 13.173 | 9.587 | 10.3155 | 12.4299 | 11.4603 | 11.4033 | 24.0081 | 2017-01-31 | 838.9998 | 823.9058 | 817.8732 | 775.5114 | [9 empty] | 0.79562 |  | 117.3989 |  | 4030.7763 |  | 207.9681 |  | 187.4867 |  | 134.0531 |  | 157.4452 |  | 158.8792
01/02 08:00:00 | 21.9796 | 22.2657 | 22.3877 | 21.7518 | 21.083 | 21.9149 | 21.5957 | 15.9569 | 12.4139 | 12.8984 | 15.2249 | 14.1254 | 13.7865 | 68.6578 | 2017-02-01 | 673.7845 | 680.6507 | 694.656 | 674.2105 | [9 empty] | 0.14735 |  | 2777.3886 |  | 0.18146 |  | 3163.3837 |  | 3109.1166 |  | 2855.0776 |  | 2973.7884 |  | 3010.8615
01/02 09:00:00 | 21.8338 | 22.1438 | 22.2766 | 21.6192 | 20.9489 | 21.7816 | 22.6288 | 15.3726 | 11.8733 | 12.3981 | 14.6129 | 43.2849 | 13.2111 | 41.9572 | 2017-02-02 | 630.6723 | 634.8384 | 692.1125 | 733.2632 | [9 empty] | 0.63208 |  | 706.7376 |  | 10524.8952 |  | 905.0401 |  | 873.7396 |  | 747.71 |  | 1.7629 |  | 826.3347
01/02 10:00:00 | 21.6886 | 22.0181 | 22.1598 | 21.4872 | 21.0403 | 21.6414 | 22.9668 | 14.3371 | 11.2823 | 11.6792 | 29.4864 | 60.6729 | 12.9553 | 9.8004 | 2017-02-03 | 803.9817 | 794.6826 | 806.2941 | 933.1902 | [9 empty] | 1.6337 |  | 20.5821 |  | 16694.8251 |  | 2.196 |  | 3.5298 |  | 387.5378 |  | 2588.0116 |  | 9.9538
01/02 11:00:00 | 21.5496 | 21.8962 | 22.0467 | 21.4783 | 21.9308 | 21.5052 | 22.6931 | 24.6204 | 11.8953 | 12.1949 | 57.9245 | 42.5117 | 39.5263 | 39.7397 | 2017-02-04 | 873.214 | 884.4245 | 892.6878 | 829.2499 | [9 empty] | 1.3075 |  | 228.5946 |  | 1932.8402 |  | 775.3142 |  | 758.7164 |  | 330.6855 |  | 7.6838 |  | 0.04558
01/02 12:00:00 | 21.5209 | 21.7863 | 21.9468 | 22.2021 | 23.3773 | 21.5979 | 22.8766 | 48.6847 | 13.7298 | 13.9994 | 43.1154 | 36.3219 | 58.6589 | 8.5429 | 2017-02-05 | 734.1641 | 701.9647 | 768.2886 | 648.2671 | [9 empty] | 1.8381 |  | 1611.3632 |  | 7378.2895 |  | 26.9045 |  | 29.7732 |  | 1195.2578 |  | 771.6725 |  | 2511.6137
01/02 13:00:00 | 21.8352 | 21.6994 | 21.8694 | 23.4925 | 23.9542 | 22.4123 | 22.7779 | 40.7198 | 17.0282 | 16.6061 | 35.8868 | 33.8578 | 41.3456 | 17.1326 | 2017-02-06 | 442.025 | 489.116 | 496.786 | 346.788 | [9 empty] | 0.88867 |  | 556.3527 |  | 9070.0757 |  | 0.010911 |  | 0.27721 |  | 351.7169 |  | 279.7323 |  | 586.2673
01/02 14:00:00 | 22.2533 | 21.6628 | 21.8472 | 24.0537 | 24.0066 | 23.8399 | 22.7134 | 35.8548 | 39.2274 | 19.7248 | 33.9926 | 29.1879 | 35.0667 | 18.452 | 2017-02-07 | 98.7832 | 110.7354 | 111.5895 | 46.8161 | [9 empty] | 0.21167 |  | 302.8594 |  | 2700.579 |  | 431.6194 |  | 1.6201 |  | 241.5112 |  | 115.2594 |  | 276.0471
01/02 15:00:00 | 22.5041 | 21.8539 | 21.8608 | 24.1274 | 24.008 | 24.4576 | 22.691 | 34.6542 | 36.4589 | 22.8011 | 31.9567 | 30.5741 | 33.41 | 17.2173 | 2017-02-08 | 303.4941 | 301.2743 | 406.2372 | 165.6314 | [9 empty] | 0.034958 |  | 304.0457 |  | 19006.1265 |  | 370.2383 |  | 31.1786 |  | 217.2491 |  | 178.404 |  | 262.2022
01/02 16:00:00 | 22.679 | 22.6848 | 21.9193 | 24.1601 | 24.0108 | 24.5489 | 22.7094 | 30.225 | 30.0339 | 25.6084 | 29.6139 | 27.9995 | 31.1279 | 16.947 | 2017-02-09 | 838.4331 | 827.9478 | 809.7034 | 823.9166 | [9 empty] | 0.0009256 |  | 176.3056 |  | 210.7296 |  | 171.2674 |  | 75.0204 |  | 160.451 |  | 122.1567 |  | 201.0989
01/02 17:00:00 | 22.7295 | 23.3526 | 22.002 | 24.137 | 23.9762 | 24.5721 | 22.6659 | 30.2476 | 27.6295 | 27.7135 | 27.6796 | 26.1879 | 29.1228 | 18.7361 | 2017-02-10 | 912.0821 | 891.0149 | 883.5166 | 856.5384 | [9 empty] | 0.0040415 |  | 132.515 |  | 3085.1085 |  | 79.0923 |  | 80.5937 |  | 79.9863 |  | 55.5292 |  | 107.8835
01/02 18:00:00 | 22.7436 | 23.5987 | 22.1056 | 24.073 | 23.9061 | 24.5495 | 22.6541 | 27.3987 | 25.7175 | 28.8796 | 26.3168 | 24.8829 | 27.5635 | 18.1588 | 2017-02-11 | 393.1648 | 402.0631 | 419.1668 | 403.1558 | [9 empty] | 0.0080073 |  | 85.3747 |  | 99.821 |  | 57.1344 |  | 114.9344 |  | 66.5531 |  | 45.2135 |  | 88.4477
01/02 19:00:00 | 22.735 | 23.6991 | 22.2026 | 23.9395 | 23.7672 | 24.4506 | 22.596 | 25.3518 | 24.3953 | 29.1993 | 24.7502 | 23.4163 | 25.8552 | 17.0992 | 2017-02-12 | 568.6749 | 512.1417 | 514.5505 | 463.1182 | [9 empty] | 0.019324 |  | 68.1057 |  | 11142.2237 |  | 53.2331 |  | 146.4128 |  | 58.5386 |  | 39.906 |  | 76.6678
01/02 20:00:00 | 22.7057 | 23.7249 | 22.2918 | 23.7792 | 23.5591 | 24.2866 | 22.5542 | 23.3536 | 22.8908 | 28.7751 | 22.562 | 21.3618 | 23.5265 | 38.6223 | 2017-02-13 | 689.221 | 646.1736 | 648.185 | 792.1754 | [9 empty] | 0.022944 |  | 233.1326 |  | 10599.6044 |  | 247.4803 |  | 96.9664 |  | 257.9333 |  | 297.9256 |  | 227.8837
01/02 21:00:00 | 22.6544 | 23.6932 | 22.3678 | 23.6043 | 23.3213 | 24.0872 | 22.6784 | 18.2654 | 16.4588 | 22.3771 | 17.3565 | 16.4332 | 18.0605 | 3.8924 | 2017-02-14 | 616.8658 | 612.7673 | 623.1617 | 478.0969 | [9 empty] | 0.00057507 |  | 206.5821 |  | 19256.8222 |  | 157.9153 |  | 341.6838 |  | 181.2825 |  | 157.2712 |  | 200.7364
01/02 22:00:00 | 22.5896 | 23.6204 | 22.4334 | 23.4079 | 23.0683 | 23.8606 | 22.5076 | 17.45 | 15.8517 | 19.9775 | 16.5078 | 15.6552 | 17.1868 | 15.1039 | 2017-02-15 | 475.5757 | 486.1579 | 521.2149 | 614.7981 | [9 empty] | 0.0067199 |  | 5.5042 |  | 19382.8713 |  | 0.55917 |  | 23.7523 |  | 1.9711 |  | 0.30396 |  | 4.3387
01/02 23:00:00 | 22.5183 | 23.499 | 22.4863 | 23.1726 | 22.8005 | 23.6212 | 22.3342 | 16.7268 | 15.2499 | 18.427 | 15.7574 | 14.9698 | 16.4037 | 15.0105 | 2017-02-16 | 802.3779 | 792.5609 | 800.6137 | 817.7593 | [9 empty] | 0.033897 |  | 2.9456 |  | 236.5867 |  | 0.057325 |  | 11.6724 |  | 0.55794 |  | 0.0016561 |  | 1.9412
01/02 24:00:00 | 22.4329 | 23.3184 | 22.5094 | 22.9336 | 22.5209 | 23.3632 | 22.1576 | 16.0304 | 14.6859 | 21.7842 | 15.0789 | 14.345 | 15.6655 | 17.1803 | 2017-02-17 | 681.9344 | 688.0912 | 690.3388 | 441.214 | [9 empty] | 0.075761 |  | 1.3222 |  | 57946.3498 |  | 6.2222 |  | 21.196 |  | 4.4159 |  | 8.0388 |  | 2.2947
01/03 01:00:00 | 22.3304 | 23.1484 | 22.5454 | 22.7019 | 22.2253 | 23.138 | 22.0292 | 15.7128 | 14.2212 | 16.9066 | 14.6777 | 13.9916 | 15.2609 | 18.1903 | 2017-02-18 | 165.4861 | 159.4757 | 156.5976 | 224.1494 | [9 empty] | 0.090758 |  | 6.138 |  | 3441.3848 |  | 15.7538 |  | 1.648 |  | 12.3385 |  | 17.6291 |  | 8.5814
01/03 02:00:00 | 22.2163 | 22.9755 | 22.5181 | 22.4585 | 21.9772 | 22.9129 | 22.0362 | 14.8277 | 13.6989 | 16.3743 | 13.8525 | 13.2618 | 14.4138 | 17.4874 | 2017-02-19 | 135.9402 | 156.3741 | 179.3533 | 141.255 | [9 empty] | 0.032447 |  | 7.074 |  | 28.2478 |  | 14.3529 |  | 1.239 |  | 13.213 |  | 17.856 |  | 9.4469
01/03 03:00:00 | 22.0937 | 22.7926 | 22.4645 | 22.2098 | 21.7402 | 22.6785 | 21.9375 | 14.5444 | 13.2454 | 15.951 | 13.4927 | 12.9165 | 13.9909 | 18.5498 | 2017-02-20 | 284.47 | 286.9358 | 294.2881 | 181.8467 | [9 empty] | 0.02441 |  | 16.0426 |  | 10531.5367 |  | 28.1368 |  | 6.7537 |  | 25.5744 |  | 31.7339 |  | 20.7835
01/03 04:00:00 | 21.9626 | 22.5987 | 22.3935 | 21.9572 | 21.4935 | 22.4335 | 21.9003 | 14.1244 | 11.0513 | 15.445 | 13.0508 | 12.4798 | 13.5298 | 18.2862 | 2017-02-21 | 118.7902 | 119.8023 | 124.7295 | 133.0824 | [9 empty] | 0.0038747 |  | 17.3201 |  | 204.2678 |  | 52.3436 |  | 8.0723 |  | 27.4094 |  | 33.7139 |  | 22.6233
01/03 05:00:00 | 21.8321 | 22.4379 | 22.3166 | 21.7144 | 21.2486 | 22.1939 | 21.9114 | 13.9971 | 11.008 | 15.0916 | 11.4622 | 11.126 | 11.9857 | 17.7706 | 2017-02-22 | 0 | 0 | 0 | 1.5799 | [9 empty] | 0.0062818 |  | 14.2393 |  | 2.4962 |  | 45.7335 |  | 7.1768 |  | 39.7961 |  | 44.1502 |  | 33.4652
01/03 06:00:00 | 21.7058 | 22.3234 | 22.2378 | 21.5203 | 21.0515 | 22.0109 | 21.8575 | 13.0988 | 10.6617 | 14.3548 | 10.8651 | 10.5526 | 11.3222 | 19.2682 | 2017-02-23 | 0 | 0 | 0 | 6.6021 | [9 empty] | 0.023025 |  | 38.0616 |  | 43.5874 |  | 74.0729 |  | 24.1419 |  | 70.6131 |  | 75.9622 |  | 63.1399
01/03 07:00:00 | 21.5861 | 22.2124 | 22.1609 | 21.3909 | 20.9192 | 21.874 | 21.8138 | 12.7233 | 10.322 | 13.8695 | 10.5769 | 10.2661 | 11.0194 | 18.1719 | 2017-02-24 | 0 | 0 | 0 | 0 | [9 empty] | 0.051839 |  | 29.6867 |  | 0 |  | 61.6208 |  | 18.5102 |  | 57.6837 |  | 62.501 |  | 51.1581
01/03 08:00:00 | 21.4615 | 22.0937 | 22.0734 | 21.2534 | 20.7773 | 21.7363 | 22.1018 | 15.746 | 13.6568 | 17.64 | 13.169 | 12.9706 | 13.8029 | 64.4003 | 2017-02-25 | 298.6509 | 277.0286 | 273.886 | 172.9463 | [9 empty] | 0.40991 |  | 2367.2351 |  | 15801.6662 |  | 2574.9056 |  | 2186.521 |  | 2624.645 |  | 2645.0083 |  | 2560.0919
01/03 09:00:00 | 21.337 | 21.9628 | 21.9823 | 21.1142 | 20.6341 | 21.5954 | 22.8983 | 26.538 | 13.0787 | 16.9736 | 28.6455 | 42.2558 | 13.2789 | 18.3507 | 2017-02-26 | 695.3168 | 629.1203 | 670.3348 | 581.0968 | [9 empty] | 2.4377 |  | 67.0313 |  | 13046.2244 |  | 27.7946 |  | 1.8965 |  | 105.9818 |  | 571.4526 |  | 25.7233
01/03 10:00:00 | 21.3055 | 21.8364 | 21.8863 | 21.0987 | 20.7167 | 21.4505 | 22.7991 | 48.1906 | 12.4605 | 16.0359 | 58.4559 | 60.1119 | 40.3714 | 13.7552 | 2017-02-27 | 445.8114 | 489.5966 | 546.7871 | 454.5496 | [9 empty] | 2.2308 |  | 1185.7933 |  | 76.3566 |  | 1.6762 |  | 5.2016 |  | 1998.1528 |  | 2148.9379 |  | 708.42
01/03 11:00:00 | 21.6014 | 21.7172 | 21.7873 | 21.8088 | 21.6822 | 21.5248 | 22.6354 | 50.296 | 11.8521 | 15.3025 | 42.363 | 56.5679 | 58.0653 | 44.0771 | 2017-02-28 | 189.5078 | 188.5301 | 184.5749 | 228.7663 | [9 empty] | 1.0692 |  | 38.6742 |  | 1541.2334 |  | 1038.4537 |  | 827.9773 |  | 2.938 |  | 156.0188 |  | 195.6705
01/03 12:00:00 | 22.0384 | 21.5852 | 21.6859 | 23.0706 | 23.2119 | 22.3672 | 22.8862 | 45.1248 | 13.1728 | 14.7527 | 36.2044 | 45.3016 | 41.8229 | 9.8495 | 2017-03-01 | 63.6295 | 54.5906 | 48.977 | 86.6267 | [9 empty] | 0.71865 |  | 1244.3463 |  | 528.8696 |  | 11.0442 |  | 24.0407 |  | 694.577 |  | 1256.8459 |  | 1022.296
01/03 13:00:00 | 22.4463 | 21.4698 | 21.586 | 23.5881 | 24.1573 | 23.7398 | 22.699 | 40.9125 | 36.7794 | 26.1752 | 30.894 | 40.726 | 35.6964 | 18.0431 | 2017-03-02 | 577.4848 | 570.8136 | 620.7585 | 531.1832 | [9 empty] | 0.063835 |  | 523.0122 |  | 2143.8374 |  | 351.0521 |  | 66.131 |  | 165.1476 |  | 514.5149 |  | 311.6402
01/03 14:00:00 | 22.7024 | 21.5657 | 21.5961 | 23.6269 | 24.3925 | 24.2599 | 22.6452 | 38.1417 | 51.414 | 48.7861 | 28.9719 | 38.1355 | 33.603 | 38.5917 | 2017-03-03 | 626.9618 | 636.1061 | 648.0875 | 699.1049 | [9 empty] | 0.0032764 |  | 0.20249 |  | 5204.6297 |  | 164.4108 |  | 103.9246 |  | 92.5406 |  | 0.20813 |  | 24.8871
01/03 15:00:00 | 22.8741 | 22.304 | 22.0041 | 23.6139 | 24.4684 | 24.2922 | 22.8977 | 30.5103 | 36.6762 | 39.8463 | 30.8609 | 35.6702 | 31.6547 | 7.0478 | 2017-03-04 | 583.7048 | 585.7136 | 591.002 | 506.6702 | [9 empty] | 0.0005587 |  | 550.4907 |  | 5934.3294 |  | 877.8423 |  | 1075.7414 |  | 567.0638 |  | 819.2414 |  | 605.4977
01/03 16:00:00 | 22.9117 | 23.691 | 22.8766 | 23.6109 | 24.5146 | 24.2983 | 22.7912 | 28.6214 | 31.1794 | 34.4639 | 27.9526 | 32.8219 | 29.1647 | 17.4583 | 2017-03-05 | 575.3768 | 561.9026 | 641.0718 | 388.0216 | [9 empty] | 0.014508 |  | 124.6145 |  | 35101.9738 |  | 188.269 |  | 289.1927 |  | 110.1309 |  | 236.0411 |  | 137.0408
01/03 17:00:00 | 22.9068 | 24.3733 | 23.4555 | 23.5705 | 24.5257 | 24.2746 | 22.6762 | 27.7987 | 29.7332 | 28.1018 | 26.5219 | 31.0291 | 27.645 | 18.5487 | 2017-03-06 | 230.9164 | 189.7073 | 185.2031 | 332.8199 | [9 empty] | 0.053153 |  | 85.5626 |  | 10384.3201 |  | 125.0939 |  | 91.262 |  | 63.5724 |  | 155.7604 |  | 82.7433
01/03 18:00:00 | 22.8888 | 24.4834 | 23.5926 | 23.4982 | 24.4932 | 24.2126 | 22.6857 | 26.2752 | 28.1089 | 26.7293 | 24.8216 | 28.9111 | 25.8286 | 33.3147 | 2017-03-07 | 27.2618 | 25.3405 | 23.2833 | 173.3721 | [9 empty] | 0.041234 |  | 49.555 |  | 21348.2284 |  | 27.1002 |  | 43.3669 |  | 72.1331 |  | 19.3919 |  | 56.0418
01/03 19:00:00 | 22.8567 | 24.5195 | 23.6002 | 23.394 | 24.4191 | 24.116 | 22.8911 | 24.6892 | 26.3408 | 25.3224 | 23.0784 | 26.758 | 23.992 | 11.5683 | 2017-03-08 | 259.1881 | 288.547 | 262.6981 | 212.333 | [9 empty] | 0.0011855 |  | 172.158 |  | 2195.4054 |  | 218.2266 |  | 189.1761 |  | 132.4834 |  | 230.7274 |  | 154.3485
01/03 20:00:00 | 22.8098 | 24.5005 | 23.5907 | 23.2591 | 24.2897 | 23.9877 | 22.8651 | 23.3102 | 24.7183 | 23.9809 | 21.5304 | 24.9138 | 22.362 | 16.4842 | 2017-03-09 | 251.0735 | 287.6379 | 304.1297 | 215.3182 | [9 empty] | 0.0030578 |  | 46.5942 |  | 1278.4441 |  | 67.7995 |  | 56.1995 |  | 25.4639 |  | 71.0575 |  | 34.5487
01/03 21:00:00 | 22.7549 | 24.4506 | 23.5738 | 23.1098 | 24.1134 | 23.8387 | 22.7642 | 18.4845 | 17.8353 | 17.5274 | 16.8085 | 19.2729 | 17.4305 | 8.7127 | 2017-03-10 | 519.9649 | 448.6304 | 461.5757 | 776.8305 | [9 empty] | 8.6196e-05 |  | 95.4886 |  | 65979.9743 |  | 83.2233 |  | 77.7003 |  | 65.542 |  | 111.5194 |  | 76.0004
01/03 22:00:00 | 22.697 | 24.3732 | 23.5516 | 22.9536 | 23.912 | 23.6826 | 22.5829 | 17.4407 | 17.1328 | 16.7699 | 15.7994 | 18.1206 | 16.3785 | 13.5087 | 2017-03-11 | 638.9281 | 596.97 | 632.531 | 647.0759 | [9 empty] | 0.013002 |  | 15.4604 |  | 66.3858 |  | 13.1338 |  | 10.6354 |  | 5.2474 |  | 21.27 |  | 8.2359
01/03 23:00:00 | 22.6475 | 24.2766 | 23.537 | 22.8104 | 23.6982 | 23.5126 | 22.4701 | 17.0524 | 16.4422 | 16.2809 | 15.294 | 17.533 | 15.851 | 14.4262 | 2017-03-12 | 702.787 | 685.699 | 691.5486 | 659.4543 | [9 empty] | 0.031486 |  | 6.897 |  | 1877.7246 |  | 4.0642 |  | 3.44 |  | 0.75299 |  | 9.6524 |  | 2.0301
01/03 24:00:00 | 22.5882 | 24.1305 | 23.5102 | 22.6616 | 23.4315 | 23.3397 | 22.4043 | 16.27 | 15.804 | 15.6249 | 12.9508 | 16.7202 | 15.0966 | 14.6121 | 2017-03-13 | 700.6674 | 709.553 | 740.2957 | 622.8021 | [9 empty] | 0.033807 |  | 2.7488 |  | 6063.0013 |  | 1.4207 |  | 1.0258 |  | 2.7598 |  | 4.4445 |  | 0.23479
01/04 01:00:00 | 22.5189 | 23.9627 | 23.4703 | 22.5258 | 23.2029 | 23.1709 | 22.2667 | 16.3279 | 15.3453 | 15.3799 | 14.7897 | 16.6074 | 15.0033 | 15.499 | 2017-03-14 | 694.9241 | 675.5934 | 686.7736 | 806.8212 | [9 empty] | 0.063625 |  | 0.68717 |  | 12520.9764 |  | 0.023596 |  | 0.014163 |  | 0.50304 |  | 1.2287 |  | 0.24566
01/04 02:00:00 | 22.4185 | 23.7888 | 23.3956 | 22.3556 | 22.9281 | 22.9575 | 22.2493 | 18.6837 | 14.9344 | 18.0228 | 14.046 | 15.9675 | 14.4564 | 15.8388 | 2017-03-15 | 829.1256 | 781.5126 | 786.7001 | 947.9779 | [9 empty] | 0.028601 |  | 8.0933 |  | 14125.8704 |  | 0.8181 |  | 4.7698 |  | 3.2142 |  | 0.016543 |  | 1.911
01/04 03:00:00 | 22.2702 | 23.583 | 23.2777 | 22.0886 | 22.5915 | 22.6951 | 22.1157 | 17.592 | 14.4716 | 16.8774 | 13.5102 | 15.3527 | 13.9178 | 18.1664 | 2017-03-16 | 657.0844 | 663.913 | 663.6561 | 725.3297 | [9 empty] | 0.023851 |  | 0.32997 |  | 4657.4173 |  | 13.6517 |  | 1.6617 |  | 21.6803 |  | 7.9171 |  | 18.0507
01/04 04:00:00 | 22.0648 | 23.3595 | 23.1065 | 21.8174 | 22.2445 | 22.4227 | 21.9956 | 14.7093 | 14.0509 | 13.7555 | 12.0307 | 15.1374 | 13.7458 | 18.3941 | 2017-03-17 | 600.878 | 609.3321 | 615.0725 | 585.2972 | [9 empty] | 0.0047878 |  | 13.5776 |  | 242.7631 |  | 18.8635 |  | 21.5167 |  | 40.4927 |  | 10.606 |  | 21.6073
01/04 05:00:00 | 21.8894 | 23.134 | 22.9524 | 21.5993 | 21.9767 | 22.1592 | 21.9157 | 14.2739 | 13.5747 | 13.6136 | 13.0694 | 14.5734 | 13.2039 | 18.0605 | 2017-03-18 | 532.0333 | 559.6101 | 570.2358 | 418.4861 | [9 empty] | 0.00068909 |  | 14.338 |  | 12892.9752 |  | 20.1222 |  | 19.7746 |  | 24.9105 |  | 12.1596 |  | 23.5867
01/04 06:00:00 | 21.7582 | 22.9093 | 22.8341 | 21.3996 | 21.7312 | 21.8944 | 21.8286 | 13.3335 | 13.0632 | 15.5239 | 12.0566 | 13.6252 | 12.3501 | 18.2922 | 2017-03-19 | 543.4328 | 560.1961 | 585.4624 | 392.9195 | [9 empty] | 0.0049589 |  | 24.5886 |  | 22654.2499 |  | 27.3422 |  | 7.6634 |  | 38.883 |  | 21.7811 |  | 35.3084
01/04 07:00:00 | 21.6204 | 22.6807 | 22.687 | 21.1267 | 21.4802 | 21.6352 | 21.7815 | 15.6659 | 12.6896 | 14.746 | 11.9174 | 13.4031 | 12.2123 | 19.2105 | 2017-03-20 | 386.2322 | 394.2223 | 405.2823 | 246.1347 | [9 empty] | 0.025946 |  | 12.5641 |  | 19627.3046 |  | 42.5218 |  | 19.9317 |  | 53.1885 |  | 33.7255 |  | 48.9734
01/04 08:00:00 | 21.4287 | 22.4335 | 22.4579 | 20.8437 | 21.1992 | 21.3585 | 21.9292 | 35.0061 | 16.2333 | 17.7987 | 38.5531 | 42.4231 | 39.9624 | 74.9638 | 2017-03-21 | 194.7427 | 194.2913 | 196.0529 | 146.2137 | [9 empty] | 0.25053 |  | 1596.618 |  | 2355.0614 |  | 3449.2785 |  | 3267.8469 |  | 1325.743 |  | 1058.8986 |  | 1225.1009
01/04 09:00:00 | 21.2996 | 22.1713 | 22.2142 | 20.7202 | 21.0823 | 21.2476 | 22.7225 | 48.815 | 20.4401 | 21.3568 | 59.0932 | 61.5919 | 60.0848 | 28.6848 | 2017-03-22 | 492.2576 | 462.5489 | 488.4655 | 428.0748 | [9 empty] | 2.0245 |  | 405.2266 |  | 4119.4397 |  | 67.9745 |  | 53.7 |  | 924.6734 |  | 1082.875 |  | 985.9627
01/04 10:00:00 | 21.5215 | 21.9097 | 21.9651 | 21.3462 | 21.8948 | 21.9591 | 22.7413 | 51.4841 | 25.6964 | 25.4055 | 57.7046 | 46.7012 | 46.431 | 21.8065 | 2017-03-23 | 342.2394 | 332.6407 | 348.6272 | 320.1231 | [9 empty] | 1.4878 |  | 880.7594 |  | 489.1296 |  | 15.131 |  | 12.9525 |  | 1288.6742 |  | 619.7435 |  | 606.3636
01/04 11:00:00 | 21.8499 | 21.7846 | 21.8418 | 22.5769 | 23.0554 | 23.11 | 22.6057 | 46.4204 | 37.9446 | 30.7596 | 47.4495 | 39.3306 | 39.2321 | 18.1897 | 2017-03-24 | 85.3873 | 82.5524 | 84.506 | 167.8217 | [9 empty] | 0.57126 |  | 796.9751 |  | 6795.4356 |  | 390.2589 |  | 158.002 |  | 856.1369 |  | 446.9404 |  | 442.7856
01/04 12:00:00 | 22.1601 | 21.9419 | 21.8372 | 23.5259 | 23.4677 | 23.5941 | 22.7354 | 40.9295 | 35.922 | 37.6351 | 41.0708 | 35.6401 | 35.2732 | 21.3073 | 2017-03-25 | 8.6274 | 9.2497 | 9.9845 | 0 | [9 empty] | 0.33096 |  | 385.0305 |  | 74.4325 |  | 213.5898 |  | 266.5973 |  | 390.5955 |  | 205.4298 |  | 195.0468
01/04 13:00:00 | 22.5812 | 22.7145 | 22.2758 | 23.9424 | 23.5751 | 23.7863 | 22.84 | 38.661 | 28.9916 | 36.1252 | 37.6962 | 32.6871 | 32.2818 | 21.6609 | 2017-03-26 | 0 | 0 | 0 | 0 | [9 empty] | 0.067005 |  | 289.0032 |  | 0 |  | 53.7398 |  | 209.2159 |  | 257.133 |  | 121.5771 |  | 112.8038
01/04 14:00:00 | 22.967 | 23.5373 | 22.8797 | 24.131 | 23.6695 | 23.9691 | 22.774 | 36.4832 | 25.7843 | 32.1407 | 35.3886 | 30.7921 | 30.3727 | 26.6022 | 2017-03-27 | 0 | 0 | 0 | 0 | [9 empty] | 0.03724 |  | 97.6333 |  | 0 |  | 0.66906 |  | 30.6741 |  | 77.1997 |  | 17.5551 |  | 14.2164
01/04 15:00:00 | 23.0821 | 23.8424 | 23.2397 | 24.2053 | 23.7099 | 24.061 | 22.601 | 35.1078 | 25.1298 | 30.3298 | 34.0411 | 29.885 | 29.494 | 28.8317 | 2017-03-28 | 23.934 | 25.8187 | 27.117 | -0.20318 | [9 empty] | 0.23148 |  | 39.3896 |  | 582.6033 |  | 13.7045 |  | 2.2442 |  | 27.1371 |  | 1.1094 |  | 0.43866
01/04 16:00:00 | 22.9335 | 23.7444 | 23.1905 | 24.0288 | 23.5096 | 23.8782 | 22.5589 | 32.679 | 23.9715 | 28.7608 | 31.4258 | 27.5819 | 27.2018 | 29.6928 | 2017-03-29 | 97.5226 | 117.1071 | 183.7515 | 0 | [9 empty] | 0.14035 |  | 8.9171 |  | 9510.6565 |  | 32.7333 |  | 0.86863 |  | 3.0031 |  | 4.4559 |  | 6.2051
01/04 17:00:00 | 22.717 | 23.5427 | 23.0279 | 23.7885 | 23.2312 | 23.6235 | 22.5611 | 29.2193 | 22.0391 | 26.0607 | 27.9788 | 24.5118 | 24.1135 | 53.9052 | 2017-03-30 | 117.1104 | 136.7581 | 181.6471 | 0 | [9 empty] | 0.02433 |  | 609.3944 |  | 13714.8468 |  | 1015.4456 |  | 775.3166 |  | 672.1791 |  | 863.971 |  | 887.5452
01/04 18:00:00 | 22.6271 | 23.4656 | 22.9727 | 23.6595 | 23.088 | 23.5133 | 22.6852 | 31.1214 | 21.5477 | 25.9131 | 28.0478 | 24.8656 | 24.5571 | 34.2079 | 2017-03-31 | 67.8386 | 77.2733 | 96.3208 | 151.4303 | [9 empty] | 0.0033826 |  | 9.5262 |  | 6987.5872 |  | 160.2798 |  | 68.8028 |  | 37.9464 |  | 87.2771 |  | 93.1373
01/04 19:00:00 | 22.3838 | 23.1938 | 22.7245 | 23.283 | 22.7113 | 23.1637 | 22.5971 | 40.1433 | 21.2696 | 25.3449 | 27.3159 | 24.3666 | 24.0479 | 65.664 | [14 empty] | 0.045494 |  | 651.3058 |  |  |  | 1970.8616 |  | 1625.6283 |  | 1470.5766 |  | 1705.4777 |  | 1731.8953
01/04 20:00:00 | 22.1914 | 22.782 | 22.3862 | 22.7946 | 22.2073 | 22.6364 | 22.6958 | 44.1303 | 20.6787 | 25.0098 | 26.5345 | 32.9786 | 31.3369 | 36.6266 | [14 empty] | 0.25444 |  | 56.3049 |  |  |  | 254.3348 |  | 134.9514 |  | 101.8511 |  | 13.308 |  | 27.9812
01/04 21:00:00 | 22.1581 | 22.4047 | 22.097 | 22.2877 | 21.7144 | 22.1676 | 22.3678 | 33.7377 | 15.4958 | 19.4858 | 20.8356 | 25.3879 | 24.7619 | 5.6381 | [14 empty] | 0.043974 |  | 789.5872 |  |  |  | 97.1744 |  | 191.7578 |  | 230.9625 |  | 390.0521 |  | 365.7198
01/04 22:00:00 | 22.1258 | 21.9997 | 21.8428 | 21.8399 | 21.4971 | 21.9469 | 21.679 | 30.5223 | 15.0783 | 17.9606 | 19.7446 | 20.8596 | 20.5483 | 25.8484 | [14 empty] | 0.19963 |  | 21.8453 |  |  |  | 115.9948 |  | 62.2174 |  | 37.2562 |  | 24.8878 |  | 28.0905
01/04 23:00:00 | 21.9722 | 21.5267 | 21.5206 | 21.3278 | 21.0463 | 21.5553 | 21.1598 | 29.2763 | 14.7153 | 17.5568 | 19.0787 | 20.6568 | 20.2966 | 27.1385 | [14 empty] | 0.66006 |  | 4.5704 |  |  |  | 154.3351 |  | 91.8079 |  | 64.9596 |  | 42.0127 |  | 46.8112
01/04 24:00:00 | 21.7595 | 21.0613 | 21.1787 | 20.7359 | 20.4411 | 21.0431 | 20.764 | 28.2466 | 14.375 | 17.1124 | 18.6639 | 40.8292 | 19.8844 | 29.6843 | [14 empty] | 0.99089 |  | 2.0668 |  |  |  | 234.3729 |  | 158.0527 |  | 121.4492 |  | 124.2097 |  | 96.0366
01/05 01:00:00 | 21.5083 | 20.6273 | 20.8317 | 20.2729 | 20.1482 | 20.6275 | 20.4811 | 27.0628 | 14.0352 | 16.6127 | 37.7978 | 48.0479 | 19.2494 | 32.8486 | [14 empty] | 1.0552 |  | 33.4747 |  |  |  | 353.9417 |  | 263.6032 |  | 24.4946 |  | 231.0179 |  | 184.9377
01/05 02:00:00 | 21.2211 | 20.1977 | 20.4807 | 20.0091 | 20.3626 | 20.2092 | 20.299 | 26.7814 | 29.5308 | 30.782 | 47.9032 | 48.2106 | 39.5249 | 32.1711 | [14 empty] | 0.85034 |  | 29.0488 |  |  |  | 6.971 |  | 1.9296 |  | 247.4996 |  | 257.2671 |  | 54.0785
01/05 03:00:00 | 20.9077 | 19.9657 | 20.27 | 20.195 | 20.6183 | 19.9643 | 20.2249 | 25.1894 | 40.1727 | 41.4289 | 47.0203 | 41.3111 | 47.834 | 32.9466 | [14 empty] | 0.46627 |  | 60.1746 |  |  |  | 52.2167 |  | 71.9492 |  | 198.0697 |  | 69.9653 |  | 221.6328
01/05 04:00:00 | 20.584 | 20.0816 | 20.4215 | 20.4428 | 20.7453 | 20.1629 | 20.0795 | 23.8691 | 39.7592 | 42.2312 | 46.7474 | 37.1479 | 46.8471 | 34.8085 | [14 empty] | 0.25453 |  | 119.6697 |  |  |  | 24.5098 |  | 55.0971 |  | 142.5375 |  | 5.4727 |  | 144.929
01/05 05:00:00 | 20.2559 | 20.2965 | 20.6737 | 20.6414 | 20.6878 | 20.4267 | 19.9874 | 33.5283 | 39.1707 | 36.9325 | 41.0471 | 34.6201 | 45.4549 | 34.6929 | [14 empty] | 0.072068 |  | 1.3563 |  |  |  | 20.0501 |  | 5.0157 |  | 40.3761 |  | 0.0053037 |  | 115.8191
01/05 06:00:00 | 20.0573 | 20.5212 | 20.8834 | 20.7698 | 20.5433 | 20.6452 | 19.9084 | 36.2247 | 35.3182 | 34.2012 | 38.7651 | 33.9748 | 41.962 | 35.674 | [14 empty] | 0.022163 |  | 0.30325 |  |  |  | 0.12663 |  | 2.169 |  | 9.5551 |  | 2.8874 |  | 39.5391
01/05 07:00:00 | 20.0214 | 20.6878 | 20.9165 | 20.7353 | 20.3188 | 20.7719 | 19.8141 | 39.5283 | 32.7714 | 33.1931 | 37.5912 | 42.2069 | 39.0776 | 36.2864 | [14 empty] | 0.042974 |  | 10.5099 |  |  |  | 12.3551 |  | 9.5684 |  | 1.7024 |  | 35.0524 |  | 7.7908
01/05 08:00:00 | 20.0366 | 20.7376 | 20.851 | 20.604 | 20.1298 | 20.7429 | 20.1633 | 49.2528 | 52.8005 | 48.6043 | 59.1779 | 65.8084 | 60.8048 | 82.3373 | [14 empty] | 0.016048 |  | 1094.5826 |  |  |  | 872.4199 |  | 1137.9111 |  | 536.3551 |  | 273.2035 |  | 463.6462
01/05 09:00:00 | 20.0525 | 21.1257 | 20.8443 | 20.7194 | 20.6923 | 21.0642 | 21.2069 | 50.0182 | 52.8535 | 54.6866 | 60.7328 | 61.7797 | 60.9383 | 66.2172 | [14 empty] | 1.3325 |  | 262.4071 |  |  |  | 178.5879 |  | 132.9544 |  | 30.0786 |  | 19.6909 |  | 27.8663
01/05 10:00:00 | 20.0737 | 21.8317 | 21.1574 | 21.2358 | 21.3639 | 21.713 | 22.1329 | 50.9625 | 47.3483 | 53.8573 | 58.8639 | 59.3211 | 53.9892 | 64.0275 | [14 empty] | 4.2403 |  | 170.6934 |  |  |  | 278.1932 |  | 103.4323 |  | 26.6618 |  | 22.1497 |  | 100.7672
01/05 11:00:00 | 20.1419 | 22.4436 | 21.7069 | 21.8365 | 21.8775 | 22.3147 | 22.8341 | 55.4324 | 44.1947 | 48.8629 | 53.4206 | 53.482 | 51.0475 | 31.5642 | [14 empty] | 7.248 |  | 569.6898 |  |  |  | 159.5283 |  | 299.2451 |  | 477.7019 |  | 480.3891 |  | 379.5982
01/05 12:00:00 | 20.5979 | 22.919 | 22.3154 | 22.4749 | 22.4776 | 22.7768 | 22.6847 | 54.7693 | 40.806 | 46.8328 | 51.3139 | 51.2114 | 46.9417 | 38.4777 | [14 empty] | 4.3547 |  | 265.4165 |  |  |  | 5.4212 |  | 69.8082 |  | 164.7696 |  | 162.1483 |  | 71.6391
01/05 13:00:00 | 21.0286 | 23.187 | 22.5891 | 22.7399 | 22.7943 | 23.0038 | 22.5971 | 54.3771 | 37.5985 | 41.7079 | 47.9715 | 47.858 | 43.4524 | 55.5982 | [14 empty] | 2.4603 |  | 1.4909 |  |  |  | 323.9895 |  | 192.9381 |  | 58.1665 |  | 59.9107 |  | 147.5192
01/05 14:00:00 | 21.1913 | 23.2389 | 22.5871 | 22.8404 | 22.8927 | 23.0405 | 22.7826 | 54.5488 | 35.4621 | 42.0434 | 43.8397 | 43.7135 | 40.7683 | 29.6995 | [14 empty] | 2.5322 |  | 617.487 |  |  |  | 33.2077 |  | 152.372 |  | 199.9462 |  | 196.3923 |  | 122.5198
01/05 15:00:00 | 21.2775 | 23.2237 | 22.5516 | 22.8258 | 22.8817 | 22.9971 | 22.6226 | 54.251 | 33.2329 | 41.8155 | 40.7884 | 40.6893 | 37.836 | 60.2549 | [14 empty] | 1.8094 |  | 36.0462 |  |  |  | 730.1901 |  | 340.0121 |  | 378.9437 |  | 382.8123 |  | 502.6085
01/05 16:00:00 | 21.3661 | 23.1671 | 22.526 | 22.7453 | 22.8067 | 22.9047 | 22.8029 | 54.4379 | 31.3683 | 47.4818 | 38.3044 | 38.2357 | 35.5919 | 35.4919 | [14 empty] | 2.0642 |  | 358.9472 |  |  |  | 17.0045 |  | 143.7566 |  | 7.9101 |  | 7.5282 |  | 0.009997
01/05 17:00:00 | 21.4363 | 23.0179 | 22.5796 | 22.5526 | 22.6271 | 22.7088 | 22.7039 | 53.3166 | 29.5275 | 40.6696 | 37.0023 | 37.0438 | 32.6248 | 62.9366 | [14 empty] | 1.607 |  | 92.5452 |  |  |  | 1116.1731 |  | 495.8197 |  | 672.5883 |  | 670.4397 |  | 918.8049
01/05 18:00:00 | 21.5106 | 22.7941 | 22.5528 | 22.2846 | 22.3761 | 22.4369 | 22.7714 | 54.5946 | 28.0936 | 47.4742 | 47.8449 | 48.7096 | 38.5549 | 45.9023 | [14 empty] | 1.5898 |  | 75.5549 |  |  |  | 317.1494 |  | 2.4706 |  | 3.7734 |  | 7.881 |  | 53.9844
01/05 19:00:00 | 21.5603 | 22.4679 | 22.5793 | 22.1843 | 22.2839 | 22.089 | 22.8652 | 54.5684 | 32.6054 | 41.3288 | 46.3062 | 47.3944 | 43.3227 | 37.3477 | [14 empty] | 1.7027 |  | 296.5514 |  |  |  | 22.4892 |  | 15.8488 |  | 80.2541 |  | 100.9354 |  | 35.7007
01/05 20:00:00 | 21.603 | 22.0656 | 22.5184 | 22.1584 | 22.2686 | 21.9441 | 22.778 | 54.6052 | 36.3976 | 42.0454 | 48.1631 | 49.2282 | 53.572 | 56.1378 | [14 empty] | 1.3805 |  | 2.349 |  |  |  | 389.6768 |  | 198.5949 |  | 63.5963 |  | 47.743 |  | 6.5831
01/05 21:00:00 | 21.636 | 21.914 | 22.451 | 22.1654 | 22.2844 | 22.0947 | 22.6589 | 43.8749 | 28.8214 | 34.6819 | 36.3902 | 36.0282 | 34.077 | 5.3881 | [14 empty] | 1.0463 |  | 1481.228 |  |  |  | 549.1162 |  | 858.1256 |  | 961.1284 |  | 938.8134 |  | 823.0493
01/05 22:00:00 | 21.6688 | 21.9089 | 22.4369 | 22.1563 | 22.2504 | 22.1749 | 21.7659 | 38.36 | 24.3269 | 31.2388 | 32.4109 | 32.0793 | 30.6844 | 24.4641 | [14 empty] | 0.0094379 |  | 193.0976 |  |  |  | 0.018808 |  | 45.897 |  | 63.1525 |  | 57.9924 |  | 38.6931
01/05 23:00:00 | 21.6519 | 21.7068 | 22.2999 | 21.9122 | 21.9376 | 21.9645 | 21.1402 | 39.5758 | 23.7822 | 30.0102 | 31.5493 | 31.3021 | 30.1049 | 28.1551 | [14 empty] | 0.26179 |  | 130.4328 |  |  |  | 19.1227 |  | 3.4413 |  | 11.5204 |  | 9.9034 |  | 3.8015
01/05 24:00:00 | 21.5933 | 21.3559 | 22.1173 | 21.5268 | 21.4906 | 21.5769 | 20.7278 | 37.9926 | 23.177 | 29.0395 | 30.6529 | 30.4597 | 29.3756 | 30.8895 | [14 empty] | 0.74901 |  | 50.4542 |  |  |  | 59.4832 |  | 3.4225 |  | 0.055986 |  | 0.1847 |  | 2.2917
01/06 01:00:00 | 21.448 | 20.9848 | 21.8882 | 21.0538 | 20.9454 | 21.1351 | 20.4295 | 36.3154 | 22.4457 | 27.9634 | 29.5292 | 29.4159 | 28.3274 | 33.3602 | [14 empty] | 1.0375 |  | 8.7334 |  |  |  | 119.1256 |  | 29.1251 |  | 14.677 |  | 15.5577 |  | 25.3294
01/06 02:00:00 | 21.232 | 20.5517 | 21.6058 | 20.5195 | 20.4167 | 20.6103 | 20.3024 | 34.774 | 21.7577 | 26.9222 | 28.5254 | 43.3048 | 27.3354 | 33.152 | [14 empty] | 0.86423 |  | 2.6309 |  |  |  | 129.8288 |  | 38.8095 |  | 21.4049 |  | 103.081 |  | 33.8326
01/06 03:00:00 | 20.9706 | 20.093 | 21.2928 | 20.0376 | 20.0064 | 20.0712 | 20.1004 | 33.1898 | 32.5513 | 25.838 | 42.0497 | 47.6947 | 41.1538 | 35.2933 | [14 empty] | 0.75739 |  | 4.4247 |  |  |  | 7.5187 |  | 89.4035 |  | 45.6485 |  | 153.794 |  | 34.3453
01/06 04:00:00 | 20.6803 | 19.8433 | 20.9636 | 19.7047 | 20.014 | 19.7952 | 19.9344 | 32.2573 | 40.2765 | 25.0985 | 47.8286 | 48.0807 | 48.17 | 36.54 | [14 empty] | 0.55629 |  | 18.3415 |  |  |  | 13.9616 |  | 130.9087 |  | 127.4323 |  | 133.1868 |  | 135.2572
01/06 05:00:00 | 20.3541 | 19.8779 | 20.6029 | 19.7606 | 20.0853 | 19.8726 | 19.7906 | 39.2626 | 40.1274 | 24.0864 | 47.5197 | 47.7464 | 47.5575 | 38.0832 | [14 empty] | 0.31753 |  | 1.3909 |  |  |  | 4.1786 |  | 195.9109 |  | 89.0463 |  | 93.377 |  | 89.7614
01/06 06:00:00 | 20.1034 | 19.975 | 20.2297 | 19.8543 | 20.1183 | 19.9905 | 19.6195 | 37.8993 | 39.9248 | 34.1378 | 47.4054 | 47.5219 | 47.3324 | 38.1869 | [14 empty] | 0.23415 |  | 0.082707 |  |  |  | 3.0205 |  | 16.3948 |  | 84.9824 |  | 87.1424 |  | 83.6401
01/06 07:00:00 | 19.9559 | 20.0604 | 19.9586 | 19.9017 | 20.0859 | 20.0591 | 19.4945 | 39.6554 | 39.8665 | 42.1227 | 47.2664 | 47.3339 | 47.1399 | 40.3125 | [14 empty] | 0.21293 |  | 0.43178 |  |  |  | 0.19891 |  | 3.2769 |  | 48.3572 |  | 49.3013 |  | 46.6134
01/06 08:00:00 | 19.8659 | 20.1138 | 19.9554 | 19.901 | 20.0198 | 20.0784 | 19.6365 | 50.5251 | 56.2216 | 55.4856 | 64.6542 | 66.7212 | 65.4739 | 76.7922 | [14 empty] | 0.05265 |  | 689.9607 |  |  |  | 423.1478 |  | 453.9712 |  | 147.3316 |  | 101.4251 |  | 128.1026
01/06 09:00:00 | 19.7708 | 20.9089 | 20.1119 | 20.5795 | 20.6309 | 20.8401 | 20.5027 | 53.5837 | 53.5875 | 56.3428 | 62.1097 | 62.72 | 62.1055 | 71.5857 | [14 empty] | 0.53558 |  | 324.0696 |  |  |  | 323.9345 |  | 232.3451 |  | 89.793 |  | 78.5994 |  | 89.8736
01/06 10:00:00 | 19.7091 | 21.5618 | 20.4479 | 21.0738 | 21.0692 | 21.3908 | 21.6207 | 56.7255 | 52.5373 | 55.017 | 59.874 | 60.259 | 59.7142 | 63.6389 | [14 empty] | 3.6541 |  | 47.7948 |  |  |  | 123.2451 |  | 74.3361 |  | 14.1744 |  | 11.4232 |  | 15.4032
01/06 11:00:00 | 19.7983 | 21.8839 | 20.8454 | 21.3681 | 21.3953 | 21.7494 | 22.6551 | 56.0317 | 50.6968 | 54.51 | 59.4493 | 59.7574 | 58.0852 | 41.1791 | [14 empty] | 8.1615 |  | 220.6004 |  |  |  | 90.5875 |  | 177.7129 |  | 333.8024 |  | 345.1557 |  | 285.8188
01/06 12:00:00 | 19.9377 | 22.2434 | 21.2474 | 21.7173 | 21.7901 | 22.1597 | 22.6505 | 55.2867 | 48.8059 | 53.65 | 56.7694 | 56.6937 | 55.7158 | 30.1861 | [14 empty] | 7.359 |  | 630.0384 |  |  |  | 346.6967 |  | 550.5542 |  | 706.6705 |  | 702.6529 |  | 651.7643
01/06 13:00:00 | 20.1493 | 22.609 | 21.6503 | 22.1039 | 22.1812 | 22.4896 | 22.6442 | 53.5014 | 46.7168 | 52.2475 | 53.0963 | 53.0827 | 52.261 | 24.5476 | [14 empty] | 6.2244 |  | 838.3238 |  |  |  | 491.4744 |  | 767.2845 |  | 815.0311 |  | 814.2549 |  | 768.0315
01/06 14:00:00 | 20.482 | 22.9977 | 22.114 | 22.484 | 22.5186 | 22.8629 | 22.6403 | 53.3885 | 40.9504 | 48.7909 | 51.6751 | 51.4274 | 46.4265 | 51.7816 | [14 empty] | 4.6585 |  | 2.5823 |  |  |  | 117.3139 |  | 8.9443 |  | 0.011347 |  | 0.12542 |  | 28.6766
01/06 15:00:00 | 21.0354 | 23.507 | 22.7658 | 22.9109 | 22.9598 | 23.3377 | 22.9198 | 52.7665 | 37.7178 | 44.3255 | 46.6988 | 46.1633 | 42.4989 | 44.2309 | [14 empty] | 3.5513 |  | 72.8565 |  |  |  | 42.4194 |  | 0.0089588 |  | 6.0905 |  | 3.7342 |  | 2.9995
01/06 16:00:00 | 21.4132 | 23.7899 | 23.0944 | 23.2043 | 23.2761 | 23.5651 | 22.8166 | 52.9828 | 35.4364 | 41.1056 | 43.1618 | 42.7811 | 40.0773 | 41.4816 | [14 empty] | 1.9697 |  | 132.2771 |  |  |  | 36.5452 |  | 0.1414 |  | 2.8231 |  | 1.6887 |  | 1.9723
01/06 17:00:00 | 21.5674 | 23.8451 | 23.1089 | 23.2523 | 23.3448 | 23.6096 | 22.6227 | 54.4412 | 33.7698 | 39.4081 | 41.4874 | 41.3315 | 38.7206 | 71.2577 | [14 empty] | 1.1136 |  | 282.793 |  |  |  | 1405.343 |  | 1014.3966 |  | 886.2702 |  | 895.5779 |  | 1058.6638
01/06 18:00:00 | 21.7304 | 23.7723 | 22.9821 | 23.1399 | 23.2598 | 23.4932 | 22.7696 | 53.976 | 32.6675 | 38.1736 | 40.2256 | 39.9284 | 37.6122 | 48.6899 | [14 empty] | 1.08 |  | 27.9431 |  |  |  | 256.719 |  | 110.5925 |  | 71.645 |  | 76.765 |  | 122.7167
01/06 19:00:00 | 21.7843 | 23.4244 | 22.6346 | 22.8106 | 22.9266 | 23.0761 | 22.7864 | 53.1217 | 31.3878 | 38.6628 | 37.8354 | 37.6042 | 35.6464 | 62.9545 | [14 empty] | 1.0043 |  | 96.6824 |  |  |  | 996.4537 |  | 590.0846 |  | 630.969 |  | 642.6332 |  | 745.7302
01/06 20:00:00 | 21.6958 | 23.0131 | 22.297 | 22.3595 | 22.482 | 22.6268 | 22.7901 | 54.0369 | 29.768 | 46.6356 | 43.823 | 44.4006 | 43.0319 | 56.0428 | [14 empty] | 1.1975 |  | 4.0238 |  |  |  | 690.3625 |  | 88.4954 |  | 149.3245 |  | 135.5418 |  | 169.2822
01/06 21:00:00 | 21.6228 | 22.6224 | 22.1855 | 21.9559 | 22.0865 | 22.2436 | 22.4924 | 41.722 | 21.8722 | 33.936 | 32.9786 | 32.8456 | 32.0853 | 5.8795 | [14 empty] | 0.75609 |  | 1284.6798 |  |  |  | 255.7665 |  | 787.1631 |  | 734.3612 |  | 727.1711 |  | 686.7399
01/06 22:00:00 | 21.554 | 22.1416 | 22.1389 | 21.7317 | 21.8374 | 22.0501 | 21.4285 | 39.4575 | 21.3372 | 31.1871 | 29.7663 | 29.5098 | 28.5917 | 27.5018 | [14 empty] | 0.015766 |  | 142.9377 |  |  |  | 38.002 |  | 13.5811 |  | 5.1278 |  | 4.0319 |  | 1.1879
01/06 23:00:00 | 21.3815 | 21.5261 | 21.9126 | 21.2468 | 21.2696 | 21.5705 | 20.6977 | 36.9072 | 20.6392 | 29.7113 | 28.2922 | 28.1035 | 27.2304 | 33.1643 | [14 empty] | 0.46766 |  | 14.0097 |  |  |  | 156.8775 |  | 11.9228 |  | 23.7365 |  | 25.611 |  | 35.2109
01/06 24:00:00 | 21.1672 | 20.9408 | 21.659 | 20.6943 | 20.646 | 20.95 | 20.2118 | 35.6551 | 20.0072 | 28.7116 | 27.6048 | 27.4679 | 26.6565 | 35.3331 | [14 empty] | 0.91276 |  | 0.10371 |  |  |  | 234.8836 |  | 43.8438 |  | 59.7267 |  | 61.8611 |  | 75.2826
01/07 01:00:00 | 20.9053 | 20.3618 | 21.3808 | 20.1143 | 19.9926 | 20.4091 | 19.902 | 34.7134 | 36.3487 | 28.0054 | 43.2842 | 44.3593 | 43.4856 | 38.6354 | [14 empty] | 1.0065 |  | 15.3815 |  |  |  | 5.229 |  | 112.9968 |  | 21.6118 |  | 32.7636 |  | 23.5246
01/07 02:00:00 | 20.5946 | 19.9409 | 21.0065 | 19.697 | 19.5169 | 19.9906 | 19.7089 | 33.253 | 40.7909 | 26.9328 | 48.8602 | 49.7153 | 48.9003 | 39.9939 | [14 empty] | 0.78447 |  | 45.4397 |  |  |  | 0.63531 |  | 170.5905 |  | 78.6112 |  | 94.5058 |  | 79.3241
01/07 03:00:00 | 20.2613 | 20.009 | 20.6211 | 19.7736 | 19.6022 | 20.0577 | 19.5553 | 40.4673 | 40.558 | 25.918 | 48.7334 | 49.2409 | 48.6998 | 40.7948 | [14 empty] | 0.49843 |  | 0.10728 |  |  |  | 0.056116 |  | 221.3207 |  | 63.0214 |  | 71.336 |  | 62.4886
01/07 04:00:00 | 20.0059 | 20.1739 | 20.2653 | 19.9055 | 19.7328 | 20.1946 | 19.4456 | 39.2921 | 40.2763 | 35.4114 | 48.6794 | 48.9092 | 48.5225 | 40.7265 | [14 empty] | 0.31388 |  | 2.0576 |  |  |  | 0.20272 |  | 28.2503 |  | 63.2489 |  | 66.9556 |  | 60.7778
01/07 05:00:00 | 19.8625 | 20.3137 | 20.0131 | 19.97 | 19.7787 | 20.2713 | 19.3404 | 48.7713 | 40.113 | 43.0756 | 48.8731 | 49.0445 | 48.6915 | 42.1877 | [14 empty] | 0.27262 |  | 43.3437 |  |  |  | 4.3044 |  | 0.78833 |  | 44.6937 |  | 47.015 |  | 42.2985
01/07 06:00:00 | 19.8978 | 20.3841 | 20.0206 | 19.9689 | 19.7564 | 20.2904 | 19.2543 | 41.0127 | 40.1951 | 43.506 | 48.386 | 48.5326 | 48.1694 | 43.0285 | [14 empty] | 0.41407 |  | 4.0634 |  |  |  | 8.0285 |  | 0.22803 |  | 28.7029 |  | 30.2947 |  | 26.4286
01/07 07:00:00 | 19.8239 | 20.4249 | 20.1027 | 19.9487 | 19.7155 | 20.2777 | 19.2184 | 44.4729 | 40.0937 | 43.845 | 48.6149 | 48.7506 | 48.3862 | 42.3107 | [14 empty] | 0.36668 |  | 4.675 |  |  |  | 4.9151 |  | 2.3539 |  | 39.7421 |  | 41.4724 |  | 36.9117
01/07 08:00:00 | 19.7673 | 20.4347 | 20.1739 | 19.8993 | 19.6358 | 20.2358 | 19.1863 | 46.8384 | 40.0469 | 43.8537 | 48.3347 | 48.4844 | 48.1055 | 44.8861 | [14 empty] | 0.33755 |  | 3.8118 |  |  |  | 23.4175 |  | 1.0657 |  | 11.8932 |  | 12.9478 |  | 10.3648
01/07 09:00:00 | 19.7619 | 20.4291 | 20.2297 | 19.84 | 19.553 | 20.1831 | 19.4969 | 57.1687 | 56.3213 | 57.2085 | 65.4964 | 67.8412 | 66.1971 | 80.1966 | [14 empty] | 0.07024 |  | 530.2861 |  |  |  | 570.0308 |  | 528.4531 |  | 216.0962 |  | 152.6562 |  | 195.9881
01/07 10:00:00 | 19.7621 | 21.0604 | 20.5468 | 20.4045 | 20.1959 | 20.8024 | 20.5379 | 57.0712 | 53.6136 | 56.6352 | 62.7258 | 63.4663 | 62.6095 | 68.9988 | [14 empty] | 0.60185 |  | 142.2671 |  |  |  | 236.7028 |  | 152.8581 |  | 39.3495 |  | 30.6082 |  | 40.8227
01/07 11:00:00 | 19.7714 | 21.6571 | 20.9859 | 20.8965 | 20.7201 | 21.3318 | 21.7287 | 56.6278 | 52.0356 | 54.8745 | 60.3245 | 60.8674 | 60.0423 | 64.5715 | [14 empty] | 3.8312 |  | 63.1025 |  |  |  | 157.1485 |  | 94.0317 |  | 18.0368 |  | 13.7201 |  | 20.5135
01/07 12:00:00 | 19.9757 | 22.2274 | 21.4911 | 21.3657 | 21.2489 | 21.9144 | 22.8211 | 55.6704 | 48.3657 | 53.7132 | 59.2237 | 59.6119 | 56.0293 | 36.5583 | [14 empty] | 8.0961 |  | 365.2734 |  |  |  | 139.4155 |  | 294.2929 |  | 513.7224 |  | 531.4703 |  | 379.122
01/07 13:00:00 | 20.3408 | 22.8332 | 22.0043 | 21.9697 | 21.8629 | 22.5367 | 22.8383 | 55.52 | 42.8589 | 50.611 | 55.7348 | 55.7628 | 53.805 | 35.9959 | [14 empty] | 6.2376 |  | 381.1913 |  |  |  | 47.1013 |  | 213.6014 |  | 389.6244 |  | 390.7321 |  | 317.1653
01/07 14:00:00 | 20.7559 | 23.2792 | 22.4966 | 22.5272 | 22.4738 | 23.0117 | 22.6484 | 54.6442 | 39.3454 | 49.0203 | 53.6408 | 53.6633 | 48.1312 | 67.6005 | [14 empty] | 3.5815 |  | 167.8642 |  |  |  | 798.3494 |  | 345.2221 |  | 194.8732 |  | 194.2439 |  | 379.0513
01/07 15:00:00 | 21.0434 | 23.4746 | 22.7505 | 22.83 | 22.8058 | 23.2978 | 22.7533 | 55.442 | 37.219 | 45.4312 | 49.6932 | 49.5345 | 44.808 | 46.8703 | [14 empty] | 2.9238 |  | 73.4737 |  |  |  | 93.1473 |  | 2.071 |  | 7.9688 |  | 7.0978 |  | 4.2534
01/07 16:00:00 | 21.2241 | 23.4559 | 22.8353 | 22.9508 | 22.9363 | 23.3168 | 22.8324 | 56.0429 | 35.4004 | 42.4344 | 45.9031 | 45.6602 | 42.3945 | 45.7204 | [14 empty] | 2.5868 |  | 106.5541 |  |  |  | 106.5026 |  | 10.7978 |  | 0.033358 |  | 0.0036237 |  | 11.0617
01/07 17:00:00 | 21.3333 | 23.2869 | 22.7032 | 22.8551 | 22.8605 | 23.1414 | 22.7026 | 53.6428 | 33.1648 | 39.2895 | 41.9896 | 41.8036 | 38.6993 | 75.3729 | [14 empty] | 1.8748 |  | 472.197 |  |  |  | 1781.5242 |  | 1302.0162 |  | 1114.4475 |  | 1126.8984 |  | 1344.9586
01/07 18:00:00 | 21.3827 | 23.12 | 22.5513 | 22.703 | 22.7306 | 22.957 | 22.796 | 56.0309 | 31.5657 | 41.7536 | 40.0426 | 39.8563 | 37.1572 | 50.7671 | [14 empty] | 1.9975 |  | 27.708 |  |  |  | 368.6926 |  | 81.2421 |  | 115.0153 |  | 119.0445 |  | 185.2282
01/07 19:00:00 | 21.3961 | 22.8028 | 22.2851 | 22.361 | 22.4116 | 22.6082 | 22.5761 | 56.449 | 30.272 | 47.99 | 47.2542 | 47.833 | 43.9889 | 73.0356 | [14 empty] | 1.3925 |  | 275.1142 |  |  |  | 1828.723 |  | 627.2819 |  | 664.6797 |  | 635.1687 |  | 843.7086
01/07 20:00:00 | 21.4009 | 22.3809 | 22.1454 | 21.9155 | 21.9802 | 22.2031 | 22.3002 | 43.5362 | 22.3891 | 34.983 | 34.9819 | 34.8545 | 33.2923 | 6.4092 | [14 empty] | 0.80874 |  | 1378.418 |  |  |  | 255.3576 |  | 816.4625 |  | 816.3993 |  | 809.136 |  | 722.7045
01/07 21:00:00 | 21.3443 | 21.8547 | 22.0598 | 21.6741 | 21.6845 | 21.9289 | 21.0468 | 40.9885 | 21.8905 | 32.392 | 31.8381 | 31.5947 | 29.9418 | 34.4749 | [14 empty] | 0.088503 |  | 42.4271 |  |  |  | 158.3661 |  | 4.3386 |  | 6.9529 |  | 8.2957 |  | 20.5489
01/07 22:00:00 | 21.1426 | 21.1785 | 21.7516 | 21.1006 | 21.0315 | 21.3305 | 20.2504 | 38.9786 | 21.299 | 31.1888 | 30.7253 | 30.5683 | 29.0216 | 36.821 | [14 empty] | 0.79601 |  | 4.6553 |  |  |  | 240.932 |  | 31.7222 |  | 37.1575 |  | 39.0963 |  | 60.8302
01/07 23:00:00 | 20.8786 | 20.4369 | 21.3039 | 20.4175 | 20.2893 | 20.6339 | 19.7732 | 36.2919 | 36.214 | 29.5339 | 42.8435 | 43.755 | 27.1908 | 40.2256 | [14 empty] | 1.222 |  | 15.4739 |  |  |  | 16.0925 |  | 114.3132 |  | 6.8533 |  | 12.4569 |  | 169.9067
01/07 24:00:00 | 20.5807 | 20.0013 | 20.9047 | 19.9786 | 19.8035 | 19.9565 | 19.5261 | 34.7696 | 41.0861 | 28.3416 | 47.9073 | 48.8353 | 42.8857 | 41.0125 | [14 empty] | 1.1123 |  | 38.9733 |  |  |  | 0.0054241 |  | 160.5509 |  | 47.5384 |  | 61.1962 |  | 3.5091
01/08 01:00:00 | 20.257 | 20.0581 | 20.5017 | 19.9759 | 19.808 | 19.571 | 19.3177 | 40.3053 | 40.1795 | 26.9732 | 47.4142 | 47.7532 | 47.949 | 42.8413 | [14 empty] | 0.88227 |  | 6.4312 |  |  |  | 7.0852 |  | 251.7981 |  | 20.9112 |  | 24.1261 |  | 26.0879
01/08 02:00:00 | 20.006 | 20.213 | 20.1665 | 20.0709 | 19.8971 | 19.6687 | 19.1281 | 46.2965 | 40.0215 | 35.8295 | 47.9372 | 48.1584 | 48.2094 | 44.4295 | [14 empty] | 0.77077 |  | 3.4854 |  |  |  | 19.4306 |  | 73.9602 |  | 12.3035 |  | 13.9043 |  | 14.2872
01/08 03:00:00 | 19.9271 | 20.3076 | 19.9307 | 20.0786 | 19.8782 | 19.8197 | 18.9423 | 41.7873 | 40.3104 | 43.456 | 49.3281 | 49.4918 | 49.3079 | 46.0794 | [14 empty] | 0.96987 |  | 18.4224 |  |  |  | 33.281 |  | 6.8823 |  | 10.5542 |  | 11.6446 |  | 10.4231
01/08 04:00:00 | 19.8055 | 20.3439 | 19.919 | 20.0085 | 19.7849 | 19.8753 | 18.7869 | 50.6823 | 40.6786 | 44.7113 | 50.467 | 50.6062 | 50.3342 | 48.6005 | [14 empty] | 1.0375 |  | 4.3338 |  |  |  | 62.7573 |  | 15.1257 |  | 3.4837 |  | 4.0226 |  | 3.0056
01/08 05:00:00 | 19.796 | 20.3403 | 19.9588 | 19.905 | 19.6586 | 19.8549 | 18.6604 | 43.8767 | 40.405 | 44.0955 | 48.7172 | 48.8974 | 48.7112 | 47.9622 | [14 empty] | 1.2896 |  | 16.6915 |  |  |  | 57.1112 |  | 14.9515 |  | 0.57003 |  | 0.87457 |  | 0.56098
01/08 06:00:00 | 19.7074 | 20.3216 | 20.0035 | 19.8154 | 19.553 | 19.8252 | 18.573 | 46.5059 | 40.1211 | 43.8018 | 48.0807 | 48.2558 | 47.999 | 48.1896 | [14 empty] | 1.2868 |  | 2.8351 |  |  |  | 65.1013 |  | 19.2531 |  | 0.011873 |  | 0.0043719 |  | 0.036335
01/08 07:00:00 | 19.6787 | 20.2905 | 20.0353 | 19.7315 | 19.4558 | 19.79 | 18.4788 | 47.8774 | 40.242 | 44.4058 | 48.9665 | 49.1249 | 48.8463 | 51.7476 | [14 empty] | 1.4398 |  | 14.9788 |  |  |  | 132.3787 |  | 53.9029 |  | 7.7348 |  | 6.8786 |  | 8.4179
01/08 08:00:00 | 19.6566 | 20.2393 | 20.0558 | 19.6294 | 19.34 | 19.7271 | 18.4105 | 47.627 | 40.3215 | 44.2693 | 48.8739 | 49.0492 | 48.7458 | 49.5392 | [14 empty] | 1.5526 |  | 3.6566 |  |  |  | 84.966 |  | 27.7722 |  | 0.44263 |  | 0.24011 |  | 0.62954
01/08 09:00:00 | 19.6312 | 20.1794 | 20.0556 | 19.5234 | 19.2208 | 19.6538 | 18.7214 | 58.4508 | 57.1495 | 58.1969 | 67.2268 | 69.5481 | 68.0413 | 80.3573 | [14 empty] | 0.82769 |  | 479.8967 |  |  |  | 538.6032 |  | 491.0852 |  | 172.4099 |  | 116.8387 |  | 151.6838
01/08 10:00:00 | 19.5857 | 20.679 | 20.2919 | 19.9807 | 19.735 | 20.2044 | 19.8416 | 57.2778 | 52.7584 | 55.6361 | 61.7736 | 62.5305 | 61.6265 | 68.2074 | [14 empty] | 0.065489 |  | 119.4554 |  |  |  | 238.6687 |  | 158.0374 |  | 41.3928 |  | 32.2261 |  | 43.3074
01/08 11:00:00 | 19.7821 | 21.7277 | 21.0822 | 20.7913 | 20.6105 | 21.2319 | 20.854 | 57.0836 | 51.0814 | 54.8308 | 61.0369 | 61.4915 | 60.636 | 66.4231 | [14 empty] | 1.1488 |  | 87.2265 |  |  |  | 235.3706 |  | 134.3818 |  | 29.0117 |  | 24.3209 |  | 33.4906
01/08 12:00:00 | 20.034 | 22.4722 | 21.6568 | 21.4138 | 21.2849 | 21.9742 | 21.5987 | 56.0477 | 49.2851 | 53.884 | 59.763 | 60.1586 | 58.0556 | 65.5798 | [14 empty] | 2.4483 |  | 90.8611 |  |  |  | 265.5189 |  | 136.7924 |  | 33.8361 |  | 29.3899 |  | 56.6142
01/08 13:00:00 | 20.2941 | 22.9072 | 22.0124 | 21.862 | 21.8071 | 22.4937 | 22.1305 | 55.1902 | 44.2009 | 51.762 | 56.9197 | 57.1036 | 55.5044 | 65.8961 | [14 empty] | 3.3722 |  | 114.6153 |  |  |  | 470.6793 |  | 199.7711 |  | 80.5757 |  | 77.3068 |  | 107.9874
01/08 14:00:00 | 20.4985 | 23.2048 | 22.3052 | 22.2519 | 22.2043 | 22.8149 | 22.5773 | 56.3271 | 40.5735 | 50.7962 | 56.5353 | 56.6721 | 51.1428 | 66.3402 | [14 empty] | 4.3213 |  | 100.2618 |  |  |  | 663.9232 |  | 241.6176 |  | 96.1375 |  | 93.4731 |  | 230.9622
01/08 15:00:00 | 20.6498 | 23.3277 | 22.4567 | 22.4805 | 22.4424 | 23.0406 | 22.7852 | 56.5861 | 38.208 | 50.4437 | 56.0358 | 56.1307 | 46.9194 | 54.7443 | [14 empty] | 4.5602 |  | 3.3922 |  |  |  | 273.4484 |  | 18.495 |  | 1.6681 |  | 1.9222 |  | 61.2289
01/08 16:00:00 | 20.7916 | 23.3558 | 22.5843 | 22.65 | 22.6243 | 23.1124 | 22.743 | 54.9507 | 35.702 | 44.2931 | 54.6879 | 54.6676 | 43.4097 | 55.1306 | [14 empty] | 3.8081 |  | 0.032375 |  |  |  | 377.4685 |  | 117.4515 |  | 0.19598 |  | 0.21439 |  | 137.3801
01/08 17:00:00 | 20.8873 | 23.3498 | 22.6103 | 22.8239 | 22.8081 | 23.1258 | 22.7366 | 56.2862 | 33.3234 | 50.2683 | 49.5841 | 48.9362 | 40.163 | 57.6708 | [14 empty] | 3.4199 |  | 1.917 |  |  |  | 592.7954 |  | 54.7963 |  | 65.3949 |  | 76.2929 |  | 306.5226
01/08 18:00:00 | 21.0718 | 23.2719 | 22.7555 | 22.973 | 22.9922 | 23.0498 | 22.5625 | 56.2712 | 31.8154 | 45.5865 | 45.5007 | 45.1914 | 37.8438 | 71.3857 | [14 empty] | 2.2222 |  | 228.4509 |  |  |  | 1565.8126 |  | 665.5997 |  | 670.0354 |  | 686.1448 |  | 1125.0598
01/08 19:00:00 | 21.1999 | 22.9246 | 22.7855 | 22.886 | 22.911 | 22.6779 | 22.5894 | 56.244 | 30.543 | 42.2097 | 42.6222 | 42.3267 | 46.5744 | 64.434 | [14 empty] | 1.9307 |  | 67.0761 |  |  |  | 1148.6055 |  | 493.9198 |  | 475.7572 |  | 488.734 |  | 318.9684
01/08 20:00:00 | 21.2209 | 22.4758 | 22.5791 | 22.5958 | 22.5955 | 22.2397 | 22.0998 | 44.7777 | 22.3837 | 31.4689 | 31.4959 | 31.3115 | 33.3335 | 9.411 | [14 empty] | 0.77243 |  | 1250.8007 |  |  |  | 168.2913 |  | 486.5514 |  | 487.7431 |  | 479.6312 |  | 572.2874
01/08 21:00:00 | 21.1957 | 21.9961 | 22.2927 | 22.0826 | 22.0339 | 22.064 | 20.8749 | 42.9998 | 21.6747 | 30.174 | 30.3919 | 30.2453 | 29.3959 | 32.5112 | [14 empty] | 0.10291 |  | 110.0107 |  |  |  | 117.4308 |  | 5.4625 |  | 4.4914 |  | 5.1345 |  | 9.7053
01/08 22:00:00 | 21.1296 | 21.3806 | 21.92 | 21.4085 | 21.2669 | 21.5664 | 20.2023 | 39.8693 | 21.0117 | 28.7716 | 28.9431 | 28.8548 | 28.4066 | 36.8641 | [14 empty] | 0.85991 |  | 9.0309 |  |  |  | 251.2993 |  | 65.4886 |  | 62.7434 |  | 64.1498 |  | 71.5289
01/08 23:00:00 | 20.9656 | 20.7785 | 21.4571 | 20.7628 | 20.5887 | 20.9656 | 19.7583 | 37.6391 | 20.2532 | 27.4842 | 27.46 | 27.4239 | 27.0209 | 39.5194 | [14 empty] | 1.4574 |  | 3.5356 |  |  |  | 371.1888 |  | 144.8464 |  | 145.4308 |  | 146.3034 |  | 156.2126
01/08 24:00:00 | 20.7401 | 20.1784 | 21.0474 | 20.107 | 19.9743 | 20.3295 | 19.4714 | 35.4873 | 35.9521 | 26.1527 | 41.1517 | 42.3053 | 41.5733 | 42.0534 | [14 empty] | 1.6095 |  | 43.1142 |  |  |  | 37.2255 |  | 252.8328 |  | 0.81301 |  | 0.063466 |  | 0.23048
01/09 01:00:00 | 20.4689 | 19.759 | 20.6243 | 19.7115 | 19.5012 | 19.8929 | 19.307 | 41.1754 | 40.7184 | 25.6085 | 47.4748 | 48.3804 | 47.4832 | 43.6971 | [14 empty] | 1.3501 |  | 6.359 |  |  |  | 8.8728 |  | 327.1966 |  | 14.271 |  | 21.9327 |  | 14.3345
01/09 02:00:00 | 20.2267 | 19.8111 | 20.1772 | 19.7464 | 19.5323 | 19.9599 | 19.1546 | 38.1952 | 40.1656 | 34.7227 | 47.227 | 47.6355 | 47.1566 | 43.3062 | [14 empty] | 1.1493 |  | 26.1228 |  |  |  | 9.8637 |  | 73.6775 |  | 15.3721 |  | 18.7423 |  | 14.8253
01/09 03:00:00 | 20.0421 | 19.9546 | 19.9044 | 19.8544 | 19.6268 | 20.0752 | 19.0307 | 48.0585 | 40.0843 | 42.6254 | 47.9466 | 48.2264 | 47.8192 | 46.81 | [14 empty] | 1.0228 |  | 1.5586 |  |  |  | 45.2358 |  | 17.5114 |  | 1.2918 |  | 2.0061 |  | 1.0184
01/09 04:00:00 | 20.0178 | 20.0654 | 19.9121 | 19.8744 | 19.6327 | 20.1144 | 18.9547 | 40.1175 | 39.8743 | 43.0419 | 47.5265 | 47.7203 | 47.3103 | 44.8453 | [14 empty] | 1.1301 |  | 22.3523 |  |  |  | 24.711 |  | 3.2523 |  | 7.1888 |  | 8.2655 |  | 6.076
01/09 05:00:00 | 19.8885 | 20.124 | 19.9943 | 19.8527 | 19.5916 | 20.1101 | 18.9271 | 43.5927 | 40.0605 | 43.3789 | 47.8699 | 48.0478 | 47.683 | 46.8831 | [14 empty] | 0.92434 |  | 10.8273 |  |  |  | 46.5486 |  | 12.28 |  | 0.97377 |  | 1.3565 |  | 0.63985
01/09 06:00:00 | 19.799 | 20.1517 | 20.0625 | 19.8032 | 19.5194 | 20.0782 | 18.9026 | 46.9037 | 40.0831 | 43.8439 | 48.4132 | 48.5732 | 48.2028 | 44.8921 | [14 empty] | 0.80359 |  | 4.0464 |  |  |  | 23.1267 |  | 1.0987 |  | 12.3977 |  | 13.55 |  | 10.9609
01/09 07:00:00 | 19.7724 | 20.1737 | 20.1242 | 19.7563 | 19.4572 | 20.0428 | 18.8421 | 47.0649 | 40.0699 | 43.8911 | 48.2035 | 48.3818 | 47.9912 | 48.0761 | [14 empty] | 0.86539 |  | 1.0225 |  |  |  | 64.0998 |  | 17.514 |  | 0.016215 |  | 0.093422 |  | 0.0072044
01/09 08:00:00 | 19.7635 | 20.1837 | 20.1825 | 19.7036 | 19.3976 | 20.0009 | 19.1687 | 55.5873 | 56.137 | 56.3875 | 64.2287 | 66.5045 | 64.9497 | 79.7919 | [14 empty] | 0.35378 |  | 585.8649 |  |  |  | 559.555 |  | 547.7693 |  | 242.2145 |  | 176.5562 |  | 220.2918
01/09 09:00:00 | 19.755 | 20.9252 | 20.5532 | 20.3649 | 20.1302 | 20.718 | 20.0011 | 55.1952 | 53.2197 | 55.6078 | 60.9972 | 61.715 | 60.9062 | 69.7731 | [14 empty] | 0.060586 |  | 212.5169 |  |  |  | 274.0158 |  | 200.6559 |  | 77.0171 |  | 64.9332 |  | 78.6228
01/09 10:00:00 | 19.7539 | 21.5555 | 21.0168 | 20.8793 | 20.6767 | 21.2832 | 20.6558 | 55.6673 | 52.5795 | 55.2531 | 60.8126 | 61.2719 | 60.575 | 67.0502 | [14 empty] | 0.81343 |  | 129.57 |  |  |  | 209.4008 |  | 139.1724 |  | 38.908 |  | 33.3887 |  | 41.9279
01/09 11:00:00 | 19.762 | 21.8679 | 21.2775 | 21.1379 | 20.9909 | 21.6007 | 21.2685 | 56.3936 | 50.0609 | 54.5443 | 59.8386 | 60.2963 | 59.6048 | 65.9969 | [14 empty] | 2.2696 |  | 92.2243 |  |  |  | 253.9553 |  | 131.1626 |  | 37.9251 |  | 32.4965 |  | 40.8596
01/09 12:00:00 | 19.8553 | 22.1971 | 21.4737 | 21.437 | 21.3575 | 21.9672 | 22.0501 | 56.5822 | 47.8725 | 54.4082 | 59.9443 | 60.2784 | 56.4752 | 64.5507 | [14 empty] | 4.8171 |  | 63.4967 |  |  |  | 278.161 |  | 102.8688 |  | 21.219 |  | 18.2521 |  | 65.2131
01/09 13:00:00 | 20.0033 | 22.4607 | 21.7541 | 21.7896 | 21.7755 | 22.3627 | 22.7772 | 57.0127 | 46.4871 | 51.277 | 56.4546 | 56.4289 | 54.4838 | 49.6445 | [14 empty] | 7.6947 |  | 54.2903 |  |  |  | 9.9693 |  | 2.665 |  | 46.3778 |  | 46.0279 |  | 23.4192
01/09 14:00:00 | 20.2247 | 22.7209 | 22.0946 | 22.1993 | 22.2054 | 22.6522 | 23.0374 | 55.3773 | 41.781 | 47.3893 | 51.9182 | 51.8494 | 51.206 | 33.195 | [14 empty] | 7.9114 |  | 492.0586 |  |  |  | 73.7206 |  | 201.4792 |  | 350.5589 |  | 347.9886 |  | 324.3991
01/09 15:00:00 | 20.572 | 23.0309 | 22.3562 | 22.5247 | 22.5129 | 22.9518 | 23.0567 | 53.5125 | 37.3192 | 44.3155 | 48.2139 | 48.0668 | 44.462 | 32.4554 | [14 empty] | 6.1738 |  | 443.404 |  |  |  | 23.6571 |  | 140.6636 |  | 248.3308 |  | 243.7153 |  | 144.1595
01/09 16:00:00 | 21.0691 | 23.3478 | 22.651 | 22.8734 | 22.8765 | 23.3315 | 22.8454 | 52.8457 | 34.3863 | 42.1623 | 43.6607 | 43.1884 | 40.0771 | 43.8864 | [14 empty] | 3.155 |  | 80.2695 |  |  |  | 90.2531 |  | 2.9727 |  | 0.050972 |  | 0.48725 |  | 14.5111
01/09 17:00:00 | 21.5335 | 23.61 | 22.9136 | 23.1677 | 23.2181 | 23.6274 | 22.8496 | 52.4566 | 32.2086 | 38.7551 | 39.7066 | 39.6622 | 37.5705 | 38.466 | [14 empty] | 1.7321 |  | 195.7342 |  |  |  | 39.1559 |  | 0.083568 |  | 1.5391 |  | 1.4308 |  | 0.80205
01/09 18:00:00 | 21.8483 | 23.7532 | 23.0792 | 23.2748 | 23.3453 | 23.7577 | 22.7169 | 49.0484 | 30.7061 | 36.6961 | 38.0872 | 37.9093 | 35.9691 | 72.2661 | [14 empty] | 0.7546 |  | 539.0641 |  |  |  | 1727.2395 |  | 1265.2278 |  | 1168.2011 |  | 1180.3926 |  | 1317.4764
01/09 19:00:00 | 22.0056 | 23.6569 | 23.0336 | 23.1877 | 23.2513 | 23.6198 | 22.9248 | 46.4647 | 29.4823 | 35.1694 | 36.3401 | 36.2257 | 34.5059 | 31.6234 | [14 empty] | 0.84502 |  | 220.2635 |  |  |  | 4.5845 |  | 12.5739 |  | 22.247 |  | 21.1807 |  | 8.3089
01/09 20:00:00 | 21.9444 | 23.4172 | 22.8489 | 22.932 | 23.0151 | 23.3454 | 22.8108 | 45.3548 | 28.053 | 33.1658 | 34.1444 | 33.994 | 32.4507 | 60.0863 | [14 empty] | 0.75059 |  | 217.0163 |  |  |  | 1026.1322 |  | 724.7127 |  | 672.9802 |  | 680.8048 |  | 763.7249
01/09 21:00:00 | 21.8307 | 23.1038 | 22.6423 | 22.5901 | 22.69 | 23.0055 | 22.7111 | 35.6343 | 20.6247 | 25.1369 | 26.2251 | 26.0508 | 25.0213 | 5.343 | [14 empty] | 0.77507 |  | 917.5658 |  |  |  | 233.5315 |  | 391.7982 |  | 436.0621 |  | 428.8142 |  | 387.2351
01/09 22:00:00 | 21.6948 | 22.722 | 22.4117 | 22.154 | 22.1965 | 22.5639 | 21.7574 | 32.7495 | 19.8684 | 23.7871 | 24.5644 | 24.4615 | 23.4387 | 26.2856 | [14 empty] | 0.0039152 |  | 41.7823 |  |  |  | 41.1805 |  | 6.2428 |  | 2.9625 |  | 3.3275 |  | 8.1048
01/09 23:00:00 | 21.5194 | 22.2805 | 22.1608 | 21.6445 | 21.6045 | 22.0293 | 21.2186 | 30.2063 | 18.9482 | 22.2319 | 22.6671 | 22.6067 | 21.6567 | 28.3605 | [14 empty] | 0.090456 |  | 3.407 |  |  |  | 88.591 |  | 37.5597 |  | 32.4149 |  | 33.1053 |  | 44.9405
01/09 24:00:00 | 21.3259 | 21.7874 | 21.8979 | 21.1656 | 21.081 | 21.5436 | 20.8818 | 28.7534 | 18.2098 | 21.2602 | 21.7216 | 21.6846 | 20.7649 | 29.3653 | [14 empty] | 0.19718 |  | 0.37445 |  |  |  | 124.446 |  | 65.6928 |  | 58.4261 |  | 58.9942 |  | 73.9677
01/10 01:00:00 | 21.1065 | 21.3085 | 21.6177 | 20.6865 | 20.6054 | 21.049 | 20.6488 | 27.7705 | 17.7246 | 20.5967 | 21.2099 | 21.1486 | 20.266 | 31.7881 | [14 empty] | 0.2095 |  | 16.1412 |  |  |  | 197.7824 |  | 125.2474 |  | 111.8969 |  | 113.199 |  | 132.7588
01/10 02:00:00 | 20.8694 | 20.903 | 21.3218 | 20.2704 | 20.1 | 20.5595 | 20.4291 | 26.2934 | 17.1335 | 19.712 | 37.9721 | 39.1264 | 19.3183 | 33.737 | [14 empty] | 0.19381 |  | 55.4071 |  |  |  | 275.6771 |  | 196.702 |  | 17.9354 |  | 29.0451 |  | 207.8994
01/10 03:00:00 | 20.6292 | 20.5712 | 21.0324 | 20.0453 | 19.8746 | 20.1692 | 20.2509 | 24.7525 | 16.4296 | 18.7272 | 43.8375 | 45.2404 | 33.57 | 34.6285 | [14 empty] | 0.14304 |  | 97.5351 |  |  |  | 331.2011 |  | 252.8505 |  | 84.8066 |  | 112.6136 |  | 1.1203
01/10 04:00:00 | 20.3963 | 20.3227 | 20.7627 | 20.3094 | 20.1551 | 20.0282 | 20.1481 | 34.1812 | 29.7446 | 15.0857 | 44.084 | 44.5625 | 44.4142 | 35.6998 | [14 empty] | 0.061598 |  | 2.3061 |  |  |  | 35.4643 |  | 424.9436 |  | 70.2946 |  | 78.5478 |  | 75.9401
01/10 05:00:00 | 20.2889 | 20.2178 | 20.5448 | 20.6094 | 20.4639 | 20.2612 | 20.1567 | 34.6498 | 38.9764 | 15.1854 | 39.3575 | 44.7612 | 44.6758 | 35.6243 | [14 empty] | 0.017494 |  | 0.94967 |  |  |  | 11.2365 |  | 417.7488 |  | 13.9373 |  | 83.4842 |  | 81.9304
01/10 06:00:00 | 20.3058 | 20.3893 | 20.3853 | 20.8207 | 20.6862 | 20.5695 | 20.0698 | 36.5802 | 38.5859 | 14.6552 | 35.5654 | 40.0137 | 38.7425 | 33.849 | [14 empty] | 0.055691 |  | 7.4592 |  |  |  | 22.4384 |  | 368.4016 |  | 2.9459 |  | 38.0038 |  | 23.9463
01/10 07:00:00 | 20.3566 | 20.6456 | 20.2196 | 20.8732 | 20.8391 | 20.8233 | 19.9521 | 37.2642 | 33.5746 | 30.8524 | 34.0174 | 36.6116 | 34.9983 | 36.6974 | [14 empty] | 0.16359 |  | 0.3212 |  |  |  | 9.7518 |  | 34.1643 |  | 7.1827 |  | 0.0073601 |  | 2.8872
01/10 08:00:00 | 20.3757 | 20.8386 | 20.1497 | 20.785 | 20.8048 | 20.8658 | 20.2168 | 46.6769 | 51.1412 | 50.1712 | 56.1244 | 59.6306 | 57.5159 | 74.4172 | [14 empty] | 0.025274 |  | 769.5234 |  |  |  | 541.7708 |  | 587.868 |  | 334.6262 |  | 218.6416 |  | 285.6523
01/10 09:00:00 | 20.3978 | 21.3593 | 20.3437 | 20.9425 | 21.1877 | 21.2837 | 21.226 | 54.3789 | 51.2695 | 52.8478 | 57.7624 | 58.4524 | 57.6796 | 66.9488 | [14 empty] | 0.68587 |  | 158.0025 |  |  |  | 245.8411 |  | 198.8385 |  | 84.3907 |  | 72.1888 |  | 85.9191
01/10 10:00:00 | 20.6284 | 22.2096 | 20.9108 | 21.6713 | 21.8371 | 22.0325 | 22.2372 | 52.6509 | 43.983 | 52.2371 | 56.3164 | 48.9233 | 48.3383 | 64.4779 | [14 empty] | 2.5882 |  | 139.8779 |  |  |  | 420.0405 |  | 149.8388 |  | 66.6102 |  | 241.9457 |  | 260.4894
01/10 11:00:00 | 20.9282 | 22.9398 | 21.7107 | 22.409 | 22.4093 | 22.6861 | 23.0078 | 51.6098 | 39.2593 | 45.6535 | 48.2461 | 43.5841 | 43.0622 | 22.92 | [14 empty] | 4.3247 |  | 823.1042 |  |  |  | 266.9708 |  | 516.81 |  | 641.4129 |  | 427.0042 |  | 405.7073
01/10 12:00:00 | 21.2449 | 23.2907 | 22.3954 | 22.9789 | 22.6925 | 23.0052 | 22.8007 | 51.4832 | 36.6319 | 41.2854 | 43.5729 | 41.6999 | 40.1126 | 59.9055 | [14 empty] | 2.4204 |  | 70.9362 |  |  |  | 541.661 |  | 346.7098 |  | 266.7561 |  | 331.4464 |  | 391.7616
01/10 13:00:00 | 21.5658 | 23.4379 | 22.6855 | 23.2057 | 22.8148 | 23.1458 | 22.946 | 51.3069 | 34.2676 | 39.0872 | 40.6912 | 38.6116 | 37.1242 | 21.9186 | [14 empty] | 1.9051 |  | 863.6742 |  |  |  | 152.4979 |  | 294.761 |  | 352.4112 |  | 278.6573 |  | 231.2102
01/10 14:00:00 | 21.8652 | 23.5191 | 22.8042 | 23.2826 | 22.8989 | 23.2157 | 22.8861 | 47.1023 | 32.0055 | 36.1788 | 37.8213 | 35.4372 | 34.5725 | 38.6965 | [14 empty] | 1.0422 |  | 70.6575 |  |  |  | 44.7693 |  | 6.3386 |  | 0.76592 |  | 10.6226 |  | 17.0068
01/10 15:00:00 | 22.1155 | 23.5571 | 22.8618 | 23.2994 | 22.9224 | 23.2371 | 22.8509 | 43.6285 | 30.0628 | 33.9456 | 35.6886 | 33.587 | 32.6908 | 53.3624 | [14 empty] | 0.54079 |  | 94.7487 |  |  |  | 542.8679 |  | 377.0088 |  | 312.3614 |  | 391.0654 |  | 427.3126
01/10 16:00:00 | 22.2486 | 23.5689 | 22.8849 | 23.2812 | 22.9148 | 23.2267 | 23.0015 | 41.2807 | 28.2771 | 31.9585 | 33.4851 | 31.5545 | 30.7208 | 10.0299 | [14 empty] | 0.5669 |  | 976.6164 |  |  |  | 332.9597 |  | 480.8653 |  | 550.1464 |  | 463.3086 |  | 428.1149
01/10 17:00:00 | 22.3352 | 23.5639 | 22.8934 | 23.2459 | 22.8876 | 23.2015 | 22.8123 | 37.8917 | 26.353 | 29.4951 | 30.5283 | 28.7742 | 27.9933 | 38.2255 | [14 empty] | 0.22763 |  | 0.11146 |  |  |  | 140.9573 |  | 76.2199 |  | 59.2468 |  | 89.3271 |  | 104.6985
01/10 18:00:00 | 22.4217 | 23.5661 | 22.9206 | 23.2264 | 22.8776 | 23.1878 | 22.7908 | 30.142 | 24.7999 | 23.9077 | 28.8651 | 27.2685 | 26.5292 | 41.2383 | [14 empty] | 0.1362 |  | 123.1279 |  |  |  | 270.2239 |  | 300.3503 |  | 153.0971 |  | 195.1574 |  | 216.3585
01/10 19:00:00 | 22.4149 | 23.5511 | 22.9021 | 23.1817 | 22.8529 | 23.1522 | 23.0134 | 28.5488 | 23.346 | 22.8696 | 26.7921 | 25.3655 | 24.6835 | 12.0668 | [14 empty] | 0.35821 |  | 271.6576 |  |  |  | 127.2194 |  | 116.7001 |  | 216.8352 |  | 176.856 |  | 159.1797
01/10 20:00:00 | 22.3958 | 23.5146 | 22.88 | 23.1019 | 22.8054 | 23.0938 | 22.7683 | 27.9803 | 21.9691 | 21.7842 | 25.0469 | 23.6864 | 23.086 | 41.069 | [14 empty] | 0.13875 |  | 171.313 |  |  |  | 364.8038 |  | 371.9029 |  | 256.7057 |  | 302.1538 |  | 323.3887
01/10 21:00:00 | 22.3722 | 23.4557 | 22.8544 | 23.0129 | 22.7333 | 23.0181 | 22.6587 | 22.6495 | 15.7786 | 15.6506 | 18.7279 | 17.6035 | 17.2571 | 4.6335 | [14 empty] | 0.082091 |  | 324.5774 |  |  |  | 124.2146 |  | 121.3767 |  | 198.6525 |  | 168.2223 |  | 159.3551
01/10 22:00:00 | 22.3456 | 23.3769 | 22.8212 | 22.9096 | 22.6087 | 22.9157 | 22.275 | 20.1801 | 15.2225 | 15.1764 | 17.9755 | 16.8957 | 16.5759 | 18.1148 | [14 empty] | 0.0049744 |  | 4.2652 |  |  |  | 8.3655 |  | 8.6347 |  | 0.019413 |  | 1.4863 |  | 2.3682
01/10 23:00:00 | 22.3057 | 23.243 | 22.7705 | 22.744 | 22.384 | 22.7494 | 21.9591 | 18.6769 | 14.5644 | 14.4597 | 16.813 | 15.8574 | 15.5166 | 19.1858 | [14 empty] | 0.12012 |  | 0.25896 |  |  |  | 21.357 |  | 22.3356 |  | 5.63 |  | 11.0781 |  | 13.4628
01/10 24:00:00 | 22.2625 | 23.1034 | 22.7179 | 22.5376 | 22.1581 | 22.5789 | 21.659 | 17.5515 | 13.9185 | 13.7123 | 15.7456 | 14.8695 | 14.5275 | 21.692 | [14 empty] | 0.36415 |  | 17.1438 |  |  |  | 60.4268 |  | 63.675 |  | 35.3594 |  | 46.5461 |  | 51.3303
01/11 01:00:00 | 22.2002 | 22.962 | 22.6474 | 22.3575 | 21.927 | 22.4077 | 21.5347 | 17.4276 | 13.4233 | 13.4399 | 15.4082 | 14.5683 | 14.2301 | 22.2491 | [14 empty] | 0.44298 |  | 23.2468 |  |  |  | 77.8945 |  | 77.6008 |  | 46.7968 |  | 58.9933 |  | 64.3035
01/11 02:00:00 | 22.1345 | 22.8088 | 22.5717 | 22.1819 | 21.7354 | 22.2285 | 21.572 | 16.9708 | 11.172 | 13.0615 | 13.009 | 14.1042 | 12.2015 | 20.9749 | [14 empty] | 0.31639 |  | 16.0329 |  |  |  | 96.0974 |  | 62.6214 |  | 63.4562 |  | 47.2067 |  | 76.973
01/11 03:00:00 | 22.0782 | 22.6888 | 22.5063 | 22.0448 | 21.5763 | 22.0916 | 21.698 | 16.1944 | 11.05 | 12.5502 | 12.6185 | 13.4143 | 13.4181 | 20.5792 | [14 empty] | 0.14455 |  | 19.2257 |  |  |  | 90.8054 |  | 64.4644 |  | 63.3716 |  | 51.3357 |  | 51.2804
01/11 04:00:00 | 22.0083 | 22.5926 | 22.4276 | 21.9319 | 21.4044 | 21.9535 | 21.6507 | 15.6505 | 10.7569 | 12.147 | 12.2394 | 12.8555 | 12.6048 | 21.2577 | [14 empty] | 0.12786 |  | 31.441 |  |  |  | 110.2661 |  | 83.0059 |  | 81.33 |  | 70.5974 |  | 74.8724
01/11 05:00:00 | 21.9291 | 22.4884 | 22.3396 | 21.8093 | 21.1966 | 21.7339 | 21.5405 | 15.4257 | 10.4684 | 11.8474 | 12.1059 | 12.6252 | 11.0061 | 21.1086 | [14 empty] | 0.15096 |  | 32.2951 |  |  |  | 113.2151 |  | 85.7707 |  | 81.0491 |  | 71.9688 |  | 102.0607
01/11 06:00:00 | 21.8349 | 22.3582 | 22.2339 | 21.6695 | 20.9761 | 21.5542 | 21.4418 | 14.5989 | 10.1819 | 11.3802 | 11.5082 | 12.0235 | 12.0721 | 22.2902 | [14 empty] | 0.15449 |  | 59.1561 |  |  |  | 146.6113 |  | 119.0284 |  | 116.2535 |  | 105.4055 |  | 104.4095
01/11 07:00:00 | 21.7211 | 22.2195 | 22.1111 | 21.5107 | 20.7349 | 21.3645 | 21.3579 | 14.4467 | 9.9665 | 11.1821 | 13.0478 | 11.8331 | 11.6888 | 23.2157 | [14 empty] | 0.13191 |  | 76.896 |  |  |  | 175.5426 |  | 144.8093 |  | 103.3862 |  | 129.5649 |  | 132.871
01/11 08:00:00 | 21.5911 | 22.0648 | 21.9703 | 21.284 | 20.4728 | 21.0963 | 21.5264 | 17.9771 | 13.3525 | 14.4897 | 38.4625 | 41.1473 | 13.264 | 67.9934 | [14 empty] | 0.0041812 |  | 2501.6329 |  |  |  | 2985.6336 |  | 2862.6491 |  | 872.0777 |  | 720.7131 |  | 2995.3135
01/11 09:00:00 | 21.4491 | 21.9008 | 21.8182 | 21.1469 | 20.4149 | 20.8812 | 22.5201 | 27.8022 | 12.8708 | 14.1014 | 57.1617 | 60.1774 | 29.241 | 43.2126 | [14 empty] | 1.147 |  | 237.4812 |  |  |  | 920.6248 |  | 847.461 |  | 194.5759 |  | 287.8027 |  | 195.207
01/11 10:00:00 | 21.3891 | 21.7325 | 21.6614 | 21.8437 | 21.3961 | 20.854 | 23.1134 | 46.6164 | 15.2129 | 33.3131 | 41.235 | 54.828 | 58.0896 | 7.087 | [14 empty] | 2.9731 |  | 1562.5669 |  |  |  | 66.0297 |  | 687.8066 |  | 1166.0828 |  | 2279.1988 |  | 2601.2605
01/11 11:00:00 | 21.6775 | 21.5831 | 21.6712 | 23.0786 | 23.0336 | 21.8051 | 22.9872 | 48.9775 | 39.9017 | 48.0353 | 35.1877 | 43.4176 | 40.8035 | 17.2055 | [14 empty] | 1.7154 |  | 1009.4564 |  |  |  | 515.1176 |  | 950.4744 |  | 323.3585 |  | 687.0733 |  | 556.8625
01/11 12:00:00 | 22.1925 | 21.6098 | 22.1624 | 23.6009 | 23.9811 | 23.3072 | 23.0537 | 42.0807 | 50.0448 | 37.6556 | 32.5416 | 37.6582 | 33.2644 | 13.5605 | [14 empty] | 0.74173 |  | 813.4023 |  |  |  | 1331.1043 |  | 580.5748 |  | 360.2817 |  | 580.6998 |  | 388.2443
01/11 13:00:00 | 22.9476 | 22.9207 | 23.2246 | 23.7656 | 24.3842 | 23.9201 | 23.2463 | 37.7901 | 33.9724 | 32.1379 | 29.795 | 35.0635 | 31.0054 | 12.3744 | [14 empty] | 0.08922 |  | 645.9575 |  |  |  | 466.4739 |  | 390.5943 |  | 303.4779 |  | 514.7968 |  | 347.1125
01/11 14:00:00 | 23.5121 | 24.7612 | 24.0035 | 23.9611 | 24.6999 | 24.242 | 23.4053 | 0 | 0 | 0 | 0 | 0 | 0 | 5.999 | [14 empty] | 0.011403 |  | 35.9875 |  |  |  | 35.9875 |  | 35.9875 |  | 35.9875 |  | 35.9875 |  | 35.9875
01/11 15:00:00 | 23.0536 | 24.8824 | 23.8006 | 23.7478 | 24.4739 | 24.0602 | 23.3358 | 0 | 0 | 0 | 0 | 0 | 0 | 16.3612 | [14 empty] | 0.079629 |  | 267.6888 |  |  |  | 267.6888 |  | 267.6888 |  | 267.6888 |  | 267.6888 |  | 267.6888
01/11 16:00:00 | 22.5637 | 24.5884 | 23.4762 | 23.4858 | 24.16 | 23.8167 | 23.2853 | 0 | 0 | 0 | 0 | 0 | 0 | 13.2605 | [14 empty] | 0.52075 |  | 175.8402 |  |  |  | 175.8402 |  | 175.8402 |  | 175.8402 |  | 175.8402 |  | 175.8402
01/11 17:00:00 | 22.3434 | 24.4104 | 23.3129 | 23.3232 | 23.9162 | 23.678 | 23.1215 | 0 | 0 | 0 | 0 | 0 | 0 | 15.3362 | [14 empty] | 0.60541 |  | 235.2005 |  |  |  | 235.2005 |  | 235.2005 |  | 235.2005 |  | 235.2005 |  | 235.2005
01/11 18:00:00 | 22.1624 | 24.2446 | 23.1635 | 23.1338 | 23.6667 | 23.5036 | 22.9458 | 0 | 0 | 0 | 0 | 0 | 0 | 16.3397 | [14 empty] | 0.6136 |  | 266.9846 |  |  |  | 266.9846 |  | 266.9846 |  | 266.9846 |  | 266.9846 |  | 266.9846
01/11 19:00:00 | 21.9761 | 24.0202 | 22.997 | 22.8817 | 23.3905 | 23.2605 | 22.6935 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6119 | [14 empty] | 0.51459 |  | 310.1787 |  |  |  | 310.1787 |  | 310.1787 |  | 310.1787 |  | 310.1787 |  | 310.1787
01/11 20:00:00 | 21.7559 | 23.7034 | 22.7889 | 22.5819 | 23.0616 | 22.9632 | 22.6265 | 0 | 0 | 0 | 0 | 0 | 0 | 34.8258 | [14 empty] | 0.75799 |  | 1212.8375 |  |  |  | 1212.8375 |  | 1212.8375 |  | 1212.8375 |  | 1212.8375 |  | 1212.8375
01/11 21:00:00 | 21.5027 | 23.3518 | 22.5432 | 22.236 | 22.6548 | 22.5889 | 22.7505 | 38.706 | 38.273 | 34.4122 | 34.3492 | 42.4022 | 36.8375 | 6.1707 | [14 empty] | 1.5569 |  | 1058.5432 |  |  |  | 1030.5533 |  | 797.5803 |  | 794.0256 |  | 1312.7174 |  | 940.4493
01/11 22:00:00 | 21.9491 | 23.5537 | 22.8961 | 22.4034 | 22.8828 | 22.7746 | 22.4663 | 29.6495 | 23.5568 | 24.0752 | 22.6524 | 26.5137 | 23.5611 | 15.3551 | [14 empty] | 0.26748 |  | 204.3301 |  |  |  | 67.2675 |  | 76.0393 |  | 53.2503 |  | 124.5143 |  | 67.3378
01/11 23:00:00 | 22.4851 | 23.9381 | 23.2397 | 22.6491 | 23.2486 | 23.0924 | 22.3762 | 0 | 0 | 0 | 0 | 0 | 0 | 15.0844 | [14 empty] | 0.011871 |  | 227.5389 |  |  |  | 227.5389 |  | 227.5389 |  | 227.5389 |  | 227.5389 |  | 227.5389
01/11 24:00:00 | 22.3122 | 23.8716 | 23.0612 | 22.5206 | 23.1175 | 22.9717 | 22.3683 | 0 | 0 | 0 | 0 | 0 | 0 | 13.7152 | [14 empty] | 0.0031488 |  | 188.1073 |  |  |  | 188.1073 |  | 188.1073 |  | 188.1073 |  | 188.1073 |  | 188.1073
01/12 01:00:00 | 21.9868 | 23.6165 | 22.8182 | 22.3093 | 22.8552 | 22.7405 | 22.3762 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3166 | [14 empty] | 0.15167 |  | 53.5323 |  |  |  | 53.5323 |  | 53.5323 |  | 53.5323 |  | 53.5323 |  | 53.5323
01/12 02:00:00 | 21.7934 | 23.3816 | 22.6621 | 22.1482 | 22.5889 | 22.5577 | 22.2877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.2443 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 03:00:00 | 21.6898 | 23.214 | 22.575 | 22.0506 | 22.4055 | 22.4432 | 22.1339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.19719 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 04:00:00 | 21.6124 | 23.1145 | 22.512 | 21.975 | 22.3027 | 22.351 | 21.9654 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.12459 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 05:00:00 | 21.5426 | 23.0199 | 22.4577 | 21.9046 | 22.2067 | 22.2643 | 21.8421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.08965 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 06:00:00 | 21.4805 | 22.9295 | 22.4087 | 21.8398 | 22.1154 | 22.1835 | 21.7494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.072309 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 07:00:00 | 21.4228 | 22.8407 | 22.3612 | 21.7786 | 22.0254 | 22.1044 | 21.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.067732 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 08:00:00 | 21.3731 | 22.7592 | 22.3216 | 21.7244 | 21.9441 | 22.0341 | 21.6351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.068612 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 09:00:00 | 21.3262 | 22.68 | 22.2836 | 21.6721 | 21.8649 | 21.966 | 21.6122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.081819 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 10:00:00 | 21.2879 | 22.609 | 22.2536 | 21.6281 | 21.7953 | 21.9088 | 21.5985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.096446 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 11:00:00 | 21.2574 | 22.5467 | 22.2307 | 21.5915 | 21.7361 | 21.8593 | 21.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.16693 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 12:00:00 | 21.2427 | 22.4809 | 22.2235 | 21.5697 | 21.692 | 21.827 | 21.7742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.28243 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 13:00:00 | 21.2318 | 22.4219 | 22.22 | 21.5519 | 21.6532 | 21.8008 | 21.9921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.57809 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 14:00:00 | 21.2877 | 22.4299 | 22.2936 | 21.5999 | 21.6697 | 21.8413 | 22.1129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.68104 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 15:00:00 | 21.341 | 22.443 | 22.3633 | 21.6464 | 21.688 | 21.882 | 22.2548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.83511 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 16:00:00 | 21.3662 | 22.4507 | 22.3965 | 21.6677 | 21.6959 | 21.9014 | 22.2189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.72711 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 17:00:00 | 21.3938 | 22.4624 | 22.4316 | 21.6917 | 21.7069 | 21.9235 | 22.1184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.52499 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 18:00:00 | 21.3939 | 22.4452 | 22.4361 | 21.6854 | 21.6873 | 21.9105 | 21.9429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.30143 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 19:00:00 | 21.3257 | 22.3636 | 22.3688 | 21.603 | 21.5855 | 21.819 | 21.9409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.37855 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/12 20:00:00 | 21.1996 | 22.228 | 22.2411 | 21.4559 | 21.4129 | 21.6629 | 22.1845 | 0 | 0 | 0 | 0 | 0 | 0 | 60.3714 | [14 empty] | 0.97005 |  | 3644.7025 |  |  |  | 3644.7025 |  | 3644.7025 |  | 3644.7025 |  | 3644.7025 |  | 3644.7025
01/12 21:00:00 | 21.0905 | 22.0749 | 22.0976 | 21.2949 | 21.2278 | 21.4918 | 22.9162 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2789 | [14 empty] | 3.3335 |  | 27.8667 |  |  |  | 27.8667 |  | 27.8667 |  | 27.8667 |  | 27.8667 |  | 27.8667
01/12 22:00:00 | 21.0059 | 21.9152 | 21.9836 | 21.1678 | 21.0831 | 21.3191 | 22.6888 | 0 | 0 | 0 | 0 | 0 | 0 | 10.095 | [14 empty] | 2.8321 |  | 101.9095 |  |  |  | 101.9095 |  | 101.9095 |  | 101.9095 |  | 101.9095 |  | 101.9095
01/12 23:00:00 | 20.8582 | 21.7312 | 21.8397 | 21.0106 | 20.9086 | 21.1203 | 22.3085 | 34.6961 | 34.9313 | 31.1073 | 31.0468 | 38.2157 | 33.2886 | 16.5274 | [14 empty] | 2.1034 |  | 330.1002 |  |  |  | 338.7035 |  | 212.5719 |  | 210.813 |  | 470.382 |  | 280.9383
01/12 24:00:00 | 21.2339 | 21.9682 | 22.1285 | 21.1224 | 21.1329 | 21.2552 | 22.0026 | 27.423 | 21.9349 | 22.2847 | 21.261 | 24.6898 | 22.1366 | 18.3581 | [14 empty] | 0.59085 |  | 82.1722 |  |  |  | 12.7935 |  | 15.4182 |  | 8.4269 |  | 40.09 |  | 14.2769
01/13 01:00:00 | 21.5296 | 22.1699 | 22.327 | 21.2099 | 21.2939 | 21.361 | 21.7553 | 26.2775 | 20.2861 | 21.2028 | 20.2503 | 23.1851 | 20.963 | 19.7068 | [14 empty] | 0.050902 |  | 43.1738 |  |  |  | 0.33555 |  | 2.238 |  | 0.2953 |  | 12.0982 |  | 1.578
01/13 02:00:00 | 21.643 | 22.2341 | 22.3689 | 21.2013 | 21.3011 | 21.3595 | 21.6403 | 24.8438 | 19.4317 | 20.1817 | 19.2562 | 22.0075 | 19.8953 | 20.2899 | [14 empty] | 7.3197e-06 |  | 20.7372 |  |  |  | 0.7366 |  | 0.011707 |  | 1.0686 |  | 2.95 |  | 0.15572
01/13 03:00:00 | 21.6706 | 22.2343 | 22.3405 | 21.1213 | 21.2384 | 21.2912 | 21.4794 | 19.9866 | 18.7031 | 16.2222 | 18.7153 | 21.3362 | 17.2145 | 21.5414 | [14 empty] | 0.036532 |  | 2.4173 |  |  |  | 8.0559 |  | 28.2934 |  | 7.9867 |  | 0.0421 |  | 18.7218
01/13 04:00:00 | 21.6148 | 22.1956 | 22.2581 | 21.006 | 21.1355 | 21.1979 | 21.3349 | 23.7904 | 18.0674 | 19.504 | 18.1992 | 20.6964 | 19.2217 | 22.9162 | [14 empty] | 0.07835 |  | 0.76422 |  |  |  | 23.5108 |  | 11.6427 |  | 22.2495 |  | 4.9274 |  | 13.6494
01/13 05:00:00 | 21.5663 | 22.1232 | 22.1785 | 20.8635 | 20.9985 | 21.0894 | 21.2649 | 18.258 | 14.9402 | 14.9967 | 15.1106 | 17.4445 | 15.7605 | 23.5967 | [14 empty] | 0.090864 |  | 28.5021 |  |  |  | 74.9358 |  | 73.9599 |  | 72.0142 |  | 37.8495 |  | 61.4067
01/13 06:00:00 | 21.4635 | 22.034 | 22.0549 | 20.7277 | 20.8662 | 20.9542 | 21.1964 | 17.6903 | 14.6988 | 14.66 | 14.7298 | 16.9242 | 15.3347 | 24.0818 | [14 empty] | 0.071331 |  | 40.8517 |  |  |  | 88.0412 |  | 88.7711 |  | 87.46 |  | 51.2306 |  | 76.5113
01/13 07:00:00 | 21.3661 | 21.9518 | 21.9463 | 20.6145 | 20.7528 | 20.8413 | 21.104 | 20.4407 | 16.6114 | 17.1756 | 17.3673 | 18.1025 | 16.5415 | 25.0398 | [14 empty] | 0.068682 |  | 21.1519 |  |  |  | 71.037 |  | 61.8453 |  | 58.8665 |  | 48.1257 |  | 72.2217
01/13 08:00:00 | 21.2572 | 21.8355 | 21.8118 | 20.46 | 20.5878 | 20.6803 | 21.3333 | 19.9695 | 21.0218 | 17.3172 | 22.3071 | 49.228 | 18.4 | 77.5379 | [14 empty] | 0.0057775 |  | 3314.1149 |  |  |  | 3194.0693 |  | 3626.526 |  | 3050.435 |  | 801.4514 |  | 3497.2859
01/13 09:00:00 | 21.0936 | 21.6817 | 21.6342 | 20.31 | 20.5846 | 20.5 | 22.3706 | 29.6632 | 21.1685 | 17.062 | 45.0492 | 60.1258 | 43.548 | 54.3251 | [14 empty] | 1.6306 |  | 608.2106 |  |  |  | 1099.3641 |  | 1388.538 |  | 86.0429 |  | 33.6483 |  | 116.1468
01/13 10:00:00 | 21.0322 | 21.5582 | 21.4802 | 20.4248 | 21.5549 | 20.5694 | 23.0714 | 47.7343 | 44.7637 | 35.8694 | 56.5518 | 55.3325 | 57.5036 | 5.5576 | [14 empty] | 4.1584 |  | 1778.871 |  |  |  | 1537.1177 |  | 918.8015 |  | 2600.4032 |  | 2477.5403 |  | 2698.386
01/13 11:00:00 | 21.3019 | 21.7859 | 21.5318 | 21.3262 | 23.0465 | 21.5406 | 22.9418 | 49.3392 | 40.4574 | 48.8989 | 53.7517 | 43.7729 | 53.4939 | 20.2617 | [14 empty] | 2.6891 |  | 845.5028 |  |  |  | 407.864 |  | 820.0861 |  | 1121.581 |  | 552.7751 |  | 1104.3762
01/13 12:00:00 | 22.0582 | 22.9375 | 22.3351 | 22.9518 | 23.9883 | 23.2445 | 22.9862 | 42.6149 | 31.2172 | 40.1623 | 43.692 | 38.8999 | 42.4975 | 8.0037 | [14 empty] | 0.86136 |  | 1197.937 |  |  |  | 538.8695 |  | 1034.1776 |  | 1273.6601 |  | 954.5772 |  | 1189.8229
01/13 13:00:00 | 22.8374 | 23.8862 | 23.6236 | 24.0914 | 24.35 | 24.4076 | 23.1073 | 38.0619 | 27.7398 | 34.4104 | 38.5909 | 35.8535 | 37.1601 | 24.8863 | [14 empty] | 0.072847 |  | 173.5963 |  |  |  | 8.1426 |  | 90.7074 |  | 187.8154 |  | 120.2783 |  | 150.6453
01/13 14:00:00 | 23.2839 | 24.3258 | 24.2138 | 24.5104 | 24.6139 | 24.9013 | 23.1781 | 34.8956 | 25.5719 | 31.3488 | 35.1229 | 32.3002 | 33.8699 | 17.701 | [14 empty] | 0.011177 |  | 295.6528 |  |  |  | 61.9498 |  | 186.2611 |  | 303.5204 |  | 213.1357 |  | 261.433
01/13 15:00:00 | 23.6224 | 24.7083 | 24.5562 | 24.8114 | 24.9188 | 25.2203 | 23.2226 | 33.6847 | 24.2537 | 29.9785 | 34.032 | 31.4537 | 32.7652 | 12.2599 | [14 empty] | 0.15986 |  | 459.0232 |  |  |  | 143.8517 |  | 313.9518 |  | 474.0278 |  | 368.4032 |  | 420.4669
01/13 16:00:00 | 23.7664 | 24.9155 | 24.7211 | 24.9652 | 25.0694 | 25.4043 | 23.0134 | 30.3041 | 22.4718 | 27.3639 | 30.501 | 28.1563 | 29.2639 | 24.8056 | [14 empty] | 0.56708 |  | 30.2329 |  |  |  | 5.4469 |  | 6.5447 |  | 32.438 |  | 11.2273 |  | 19.8761
01/13 17:00:00 | 23.8298 | 25.0129 | 24.8153 | 25.0418 | 25.143 | 25.5015 | 22.7938 | 29.2882 | 21.2111 | 26.1172 | 29.218 | 27.0843 | 28.1429 | 26.541 | [14 empty] | 1.0733 |  | 7.5475 |  |  |  | 28.4077 |  | 0.17956 |  | 7.1667 |  | 0.29526 |  | 2.5662
01/13 18:00:00 | 23.8193 | 25.0416 | 24.8412 | 25.0404 | 25.1252 | 25.5006 | 22.5348 | 28.8367 | 20.8689 | 25.5848 | 28.6053 | 26.6667 | 28.4631 | 45.623 | [14 empty] | 1.6499 |  | 281.7775 |  |  |  | 612.7628 |  | 401.5303 |  | 289.6016 |  | 359.3399 |  | 294.4623
01/13 19:00:00 | 23.6469 | 24.8523 | 24.6975 | 24.8457 | 24.9136 | 25.3171 | 22.689 | 28.6185 | 20.5456 | 25.1576 | 28.0852 | 26.2257 | 27.7648 | 27.9467 | [14 empty] | 0.91768 |  | 0.45138 |  |  |  | 54.7758 |  | 7.7787 |  | 0.019195 |  | 2.9616 |  | 0.033089
01/13 20:00:00 | 23.4015 | 24.5261 | 24.4452 | 24.4954 | 24.5309 | 25.0031 | 22.6013 | 27.6428 | 20.0384 | 24.3722 | 27.1724 | 25.4489 | 26.8262 | 46.809 | [14 empty] | 0.64028 |  | 367.3431 |  |  |  | 716.6631 |  | 503.4089 |  | 385.5945 |  | 456.2501 |  | 399.3092
01/13 21:00:00 | 23.1776 | 24.1932 | 24.1844 | 24.1351 | 24.1296 | 24.6524 | 22.6855 | 21.9325 | 15.0267 | 18.4594 | 20.967 | 19.6684 | 20.669 | 5.384 | [14 empty] | 0.24212 |  | 273.8517 |  |  |  | 92.9812 |  | 170.9642 |  | 242.8291 |  | 204.0427 |  | 233.6313
01/13 22:00:00 | 22.9494 | 23.8896 | 23.96 | 23.8066 | 23.718 | 24.2643 | 22.103 | 21.066 | 14.6411 | 17.8187 | 20.1761 | 18.9821 | 19.9166 | 19.4476 | [14 empty] | 0.71631 |  | 2.6189 |  |  |  | 23.1026 |  | 2.6535 |  | 0.53065 |  | 0.21672 |  | 0.21988
01/13 23:00:00 | 22.7058 | 23.5727 | 23.7302 | 23.429 | 23.2518 | 23.8277 | 21.6983 | 20.4575 | 14.2872 | 17.3244 | 19.6719 | 18.5696 | 19.4565 | 22.1731 | [14 empty] | 1.015 |  | 2.9435 |  |  |  | 62.1881 |  | 23.5101 |  | 6.2563 |  | 12.9856 |  | 7.3801
01/13 24:00:00 | 22.442 | 23.2368 | 23.4813 | 22.9698 | 22.7057 | 23.3819 | 21.455 | 19.9154 | 13.9584 | 16.8749 | 19.2178 | 18.1886 | 19.0005 | 22.9941 | [14 empty] | 0.97417 |  | 9.4779 |  |  |  | 81.6433 |  | 37.4437 |  | 14.2598 |  | 23.0922 |  | 15.9485
01/14 01:00:00 | 22.1692 | 22.8919 | 23.22 | 22.5977 | 22.2716 | 22.9384 | 21.2752 | 18.9494 | 13.5192 | 16.1936 | 18.3082 | 17.3907 | 18.1544 | 24.2518 | [14 empty] | 0.79932 |  | 28.1162 |  |  |  | 115.1893 |  | 64.9352 |  | 35.3266 |  | 47.0749 |  | 37.1785
01/14 02:00:00 | 21.8988 | 22.6139 | 22.9589 | 22.2346 | 21.9101 | 22.5833 | 21.0973 | 18.2056 | 13.1115 | 15.6099 | 17.6046 | 16.7428 | 17.4677 | 26.2908 | [14 empty] | 0.64236 |  | 65.3696 |  |  |  | 173.6921 |  | 114.0801 |  | 75.4493 |  | 91.1643 |  | 77.8467
01/14 03:00:00 | 21.6254 | 22.3558 | 22.6929 | 21.9371 | 21.5447 | 22.2279 | 20.9276 | 17.9779 | 12.7891 | 15.3325 | 17.4149 | 16.5888 | 17.2725 | 27.1795 | [14 empty] | 0.48689 |  | 84.6686 |  |  |  | 207.0823 |  | 140.3506 |  | 95.3459 |  | 112.1627 |  | 98.1478
01/14 04:00:00 | 21.3386 | 22.0307 | 22.4085 | 21.591 | 21.1545 | 21.8499 | 20.8074 | 17.3668 | 12.5062 | 14.8804 | 16.8442 | 16.0735 | 16.7105 | 27.7204 | [14 empty] | 0.28222 |  | 107.1978 |  |  |  | 231.4733 |  | 164.8661 |  | 118.2922 |  | 135.6521 |  | 121.2183
01/14 05:00:00 | 21.052 | 21.7086 | 22.1238 | 21.2509 | 20.8352 | 21.5384 | 20.7352 | 14.256 | 12.1127 | 12.1988 | 16.1853 | 15.4671 | 16.0661 | 28.5313 | [14 empty] | 0.10035 |  | 203.7842 |  |  |  | 269.5704 |  | 266.7501 |  | 152.4237 |  | 170.6711 |  | 155.3811
01/14 06:00:00 | 20.8184 | 21.425 | 21.8932 | 20.9503 | 20.5421 | 21.2519 | 20.6993 | 14.0337 | 11.7473 | 12.1154 | 15.6773 | 15.0206 | 15.5972 | 29.5076 | [14 empty] | 0.014172 |  | 239.4441 |  |  |  | 315.431 |  | 302.4891 |  | 191.2786 |  | 209.8733 |  | 193.4991
01/14 07:00:00 | 20.6412 | 21.1431 | 21.7171 | 20.6485 | 20.2428 | 20.958 | 20.7189 | 12.823 | 9.7848 | 11.3777 | 12.8893 | 12.52 | 12.8938 | 28.7223 | [14 empty] | 0.0060271 |  | 252.7887 |  |  |  | 358.6314 |  | 300.8363 |  | 250.6862 |  | 262.5173 |  | 250.5438
01/14 08:00:00 | 20.4726 | 20.9317 | 21.5513 | 20.4201 | 20.0167 | 20.7351 | 20.7341 | 12.6202 | 9.6661 | 11.0997 | 12.7548 | 34.0801 | 12.7529 | 27.2691 | [14 empty] | 0.068415 |  | 214.59 |  |  |  | 309.8658 |  | 261.4489 |  | 210.6645 |  | 46.3902 |  | 210.7216
01/14 09:00:00 | 20.3027 | 20.7815 | 21.382 | 20.2537 | 20.0031 | 20.5697 | 21.1641 | 26.9461 | 12.5457 | 13.8293 | 31.0823 | 63.0675 | 15.5244 | 82.5515 | [14 empty] | 0.74195 |  | 3091.9657 |  |  |  | 4900.8195 |  | 4722.7467 |  | 2649.0844 |  | 379.6281 |  | 4492.6376
01/14 10:00:00 | 20.2343 | 20.6318 | 21.2084 | 20.209 | 20.8454 | 20.4012 | 22.3195 | 50.3016 | 26.477 | 26.0812 | 60.6701 | 60.0044 | 42.9359 | 61.0367 | [14 empty] | 4.3479 |  | 115.2423 |  |  |  | 1194.3685 |  | 1221.8862 |  | 0.1344 |  | 1.0655 |  | 327.6369
01/14 11:00:00 | 20.5031 | 20.593 | 21.1569 | 20.8437 | 22.0816 | 20.4409 | 23.0102 | 53.4744 | 54.5239 | 50.2106 | 59.6204 | 49.9352 | 60.9068 | 17.1608 | [14 empty] | 6.2855 |  | 1318.6782 |  |  |  | 1396.0014 |  | 1092.2861 |  | 1802.8174 |  | 1074.159 |  | 1913.7092
01/14 12:00:00 | 20.907 | 21.1763 | 21.4707 | 22.1243 | 23.0165 | 21.1365 | 22.8591 | 54.3302 | 51.2684 | 52.6316 | 49.3267 | 44.0271 | 58.9793 | 25 | [14 empty] | 3.8106 |  | 860.2662 |  |  |  | 690.0306 |  | 763.5059 |  | 591.7897 |  | 362.0328 |  | 1154.5961
01/14 13:00:00 | 21.3491 | 22.5004 | 22.1976 | 23.1571 | 23.3313 | 22.5884 | 22.8094 | 54.3518 | 40.349 | 44.3153 | 43.6975 | 40.8513 | 47.6131 | 24.8514 | [14 empty] | 2.1326 |  | 870.2731 |  |  |  | 240.1759 |  | 378.8421 |  | 355.1741 |  | 255.9982 |  | 518.0973
01/14 14:00:00 | 21.7942 | 23.7304 | 23.1583 | 23.5069 | 23.4548 | 23.6994 | 22.803 | 48.5819 | 35.9557 | 39.1957 | 39.6494 | 37.1188 | 41.5397 | 23.6586 | [14 empty] | 1.0177 |  | 621.1677 |  |  |  | 151.2167 |  | 241.4002 |  | 255.7049 |  | 181.1772 |  | 319.7315
01/14 15:00:00 | 22.2753 | 24.2486 | 23.6615 | 23.6228 | 23.5415 | 24.0374 | 22.7292 | 44.3283 | 34.0921 | 36.5529 | 36.9425 | 34.5687 | 39.0308 | 24.5349 | [14 empty] | 0.20604 |  | 391.7785 |  |  |  | 91.3388 |  | 144.4311 |  | 153.9483 |  | 100.676 |  | 210.1306
01/14 16:00:00 | 22.5853 | 24.4014 | 23.819 | 23.6734 | 23.5816 | 24.1477 | 22.7444 | 35.5256 | 32.0131 | 29.4623 | 34.657 | 32.4921 | 36.6128 | 35.1227 | [14 empty] | 0.025317 |  | 0.16232 |  |  |  | 9.6697 |  | 32.0403 |  | 0.21685 |  | 6.9204 |  | 2.2202
01/14 17:00:00 | 22.6425 | 24.4703 | 23.8255 | 23.659 | 23.5591 | 24.1831 | 22.8075 | 37.168 | 30.0884 | 28.153 | 32.3574 | 30.3769 | 34.1097 | 25.6571 | [14 empty] | 0.027228 |  | 132.501 |  |  |  | 19.6364 |  | 6.2295 |  | 44.8936 |  | 22.2758 |  | 71.4455
01/14 18:00:00 | 22.6201 | 24.4753 | 23.778 | 23.562 | 23.457 | 24.1394 | 22.6988 | 36.9179 | 28.392 | 31.7953 | 30.6929 | 28.861 | 32.3029 | 43.0424 | [14 empty] | 0.0061948 |  | 37.509 |  |  |  | 214.6337 |  | 126.4978 |  | 152.5098 |  | 201.1107 |  | 115.3364
01/14 19:00:00 | 22.5805 | 24.4054 | 23.7304 | 23.3789 | 23.268 | 24.0125 | 22.8255 | 36.5192 | 26.7711 | 29.2551 | 28.6278 | 26.9906 | 30.076 | 20.0656 | [14 empty] | 0.060021 |  | 270.7221 |  |  |  | 44.9643 |  | 84.4472 |  | 73.3114 |  | 47.9567 |  | 100.2082
01/14 20:00:00 | 22.5436 | 24.2709 | 23.6324 | 23.1503 | 23.0341 | 23.8261 | 22.5109 | 29.8549 | 19.4997 | 22.0292 | 21.9928 | 20.6657 | 22.9374 | 10.3541 | [14 empty] | 0.0010658 |  | 380.2789 |  |  |  | 83.6412 |  | 136.3072 |  | 135.4587 |  | 106.3279 |  | 158.3382
01/14 21:00:00 | 22.5083 | 24.0656 | 23.5003 | 22.897 | 22.7426 | 23.5692 | 22.1323 | 27.5369 | 18.8931 | 17.7691 | 21.449 | 20.2556 | 22.4138 | 18.1208 | [14 empty] | 0.14135 |  | 88.6619 |  |  |  | 0.59635 |  | 0.12373 |  | 11.0764 |  | 4.5573 |  | 18.4291
01/14 22:00:00 | 22.4635 | 23.789 | 23.3511 | 22.601 | 22.3661 | 23.2318 | 21.8565 | 25.4088 | 18.2077 | 17.488 | 20.3927 | 19.2897 | 21.3056 | 20.1874 | [14 empty] | 0.36839 |  | 27.2623 |  |  |  | 3.9195 |  | 7.2869 |  | 0.042142 |  | 0.80589 |  | 1.2504
01/14 23:00:00 | 22.4028 | 23.4939 | 23.2309 | 22.248 | 21.9949 | 22.8865 | 21.6572 | 24.1195 | 17.4907 | 16.7228 | 19.18 | 18.1755 | 20.0428 | 20.946 | [14 empty] | 0.55593 |  | 10.0713 |  |  |  | 11.939 |  | 17.8356 |  | 3.1188 |  | 7.6754 |  | 0.81572
01/14 24:00:00 | 22.3261 | 23.2388 | 23.1015 | 21.9622 | 21.6873 | 22.5986 | 21.4914 | 23.1601 | 16.7883 | 16.1247 | 18.3111 | 17.3807 | 19.1206 | 22.3324 | [14 empty] | 0.69659 |  | 0.68514 |  |  |  | 30.7368 |  | 38.5352 |  | 16.1712 |  | 24.5188 |  | 10.3158
01/15 01:00:00 | 22.2375 | 23.0339 | 22.9654 | 21.73 | 21.3839 | 22.3097 | 21.3773 | 22.08 | 16.1471 | 15.5221 | 17.4319 | 16.5511 | 18.1844 | 22.8721 | [14 empty] | 0.73985 |  | 0.62739 |  |  |  | 45.2259 |  | 54.0224 |  | 29.5956 |  | 39.9558 |  | 21.9751
01/15 02:00:00 | 22.1364 | 22.8374 | 22.8209 | 21.5034 | 21.1335 | 22.0707 | 21.2794 | 21.5949 | 15.5984 | 15.1761 | 16.9597 | 16.1057 | 17.7017 | 23.8934 | [14 empty] | 0.73437 |  | 5.2831 |  |  |  | 68.8071 |  | 75.9919 |  | 48.0765 |  | 60.6482 |  | 38.3373
01/15 03:00:00 | 22.0256 | 22.6305 | 22.6711 | 21.2668 | 20.8892 | 21.8375 | 21.1363 | 20.9345 | 15.1198 | 14.8046 | 16.4308 | 15.6643 | 17.1342 | 25.3916 | [14 empty] | 0.7909 |  | 19.8655 |  |  |  | 105.5097 |  | 112.0839 |  | 80.2951 |  | 94.6198 |  | 68.1845
01/15 04:00:00 | 21.8946 | 22.4017 | 22.5047 | 21.0064 | 20.6219 | 21.578 | 20.9904 | 19.5352 | 14.5485 | 14.0889 | 15.329 | 14.6313 | 16.0115 | 26.3102 | [14 empty] | 0.81766 |  | 45.9008 |  |  |  | 138.3376 |  | 149.3604 |  | 120.5857 |  | 136.3968 |  | 106.0621
01/15 05:00:00 | 21.749 | 22.1551 | 22.3266 | 20.7256 | 20.3336 | 21.2982 | 20.8486 | 23.429 | 14.2004 | 16.6709 | 15.4681 | 34.602 | 16.0827 | 27.4527 | [14 empty] | 0.81087 |  | 16.1907 |  |  |  | 175.6241 |  | 116.2479 |  | 143.6322 |  | 51.1125 |  | 129.2787
01/15 06:00:00 | 21.567 | 21.885 | 22.0872 | 20.4221 | 20.1793 | 20.9913 | 20.7245 | 21.252 | 13.6653 | 15.4117 | 32.2963 | 45.9254 | 14.887 | 29.5601 | [14 empty] | 0.70978 |  | 69.0246 |  |  |  | 252.6442 |  | 200.1755 |  | 7.4868 |  | 267.8224 |  | 215.2993
01/15 07:00:00 | 21.3058 | 21.6046 | 21.7666 | 20.271 | 20.3912 | 20.6769 | 20.626 | 19.8959 | 13.1217 | 12.2822 | 44.0496 | 45.0156 | 13.9804 | 28.9808 | [14 empty] | 0.46208 |  | 82.5348 |  |  |  | 251.5085 |  | 278.8414 |  | 227.0688 |  | 257.1158 |  | 225.0105
01/15 08:00:00 | 21.0414 | 21.3171 | 21.5058 | 20.4933 | 20.7038 | 20.3605 | 20.5672 | 19.2583 | 12.7162 | 12.2437 | 44.6361 | 38.633 | 32.499 | 29.1331 | [14 empty] | 0.22488 |  | 97.5111 |  |  |  | 269.5135 |  | 285.2535 |  | 240.3431 |  | 90.2487 |  | 11.3291
01/15 09:00:00 | 20.7735 | 21.0238 | 21.3106 | 20.8139 | 20.965 | 20.2031 | 20.9199 | 17.646 | 14.0606 | 14.3854 | 58.0285 | 56.6126 | 59.4961 | 77.0273 | [14 empty] | 0.021442 |  | 3526.1415 |  |  |  | 3964.8023 |  | 3924.007 |  | 360.952 |  | 416.7589 |  | 307.3439
01/15 10:00:00 | 20.5559 | 20.7908 | 21.1252 | 21.8692 | 21.8796 | 20.9799 | 22.286 | 37.0478 | 41.4513 | 36.5333 | 46.0968 | 46.5177 | 54.02 | 59.624 | [14 empty] | 2.9931 |  | 509.6842 |  |  |  | 330.2469 |  | 533.179 |  | 182.9845 |  | 171.7742 |  | 31.4042
01/15 11:00:00 | 20.6407 | 20.8994 | 21.1751 | 23.1106 | 23.0066 | 22.5622 | 23.3277 | 48.3484 | 50.65 | 48.8694 | 42.8875 | 41.6453 | 45.4005 | 5.9374 | [14 empty] | 7.22 |  | 1798.6904 |  |  |  | 1999.2127 |  | 1843.1544 |  | 1365.3085 |  | 1275.0542 |  | 1557.3293
01/15 12:00:00 | 21.1415 | 21.9651 | 21.8162 | 23.6172 | 23.506 | 23.6997 | 23.2691 | 48.1681 | 37.5898 | 39.9571 | 38.0088 | 36.7715 | 37.7936 | 16.9283 | [14 empty] | 4.5268 |  | 975.9263 |  |  |  | 426.8967 |  | 530.3269 |  | 444.3875 |  | 393.7538 |  | 435.3596
01/15 13:00:00 | 22.3388 | 23.8356 | 23.2834 | 24.0545 | 23.9518 | 24.4443 | 23.2973 | 41.5812 | 31.5182 | 34.158 | 35.3209 | 34.179 | 35.5042 | 20.1186 | [14 empty] | 0.91859 |  | 460.6408 |  |  |  | 129.9496 |  | 197.1035 |  | 231.1102 |  | 197.6938 |  | 236.7173
01/15 14:00:00 | 23.201 | 24.7531 | 24.0333 | 24.3273 | 24.2445 | 24.7966 | 23.2883 | 38.6199 | 30.0074 | 32.4336 | 33.7233 | 32.8223 | 34.299 | 21.0627 | [14 empty] | 0.0076157 |  | 308.255 |  |  |  | 80.0087 |  | 129.2972 |  | 160.292 |  | 138.2895 |  | 175.2013
01/15 15:00:00 | 23.3867 | 24.9351 | 24.1892 | 24.4122 | 24.3474 | 24.9218 | 23.2631 | 36.5487 | 28.5389 | 30.592 | 31.6203 | 30.7933 | 32.2986 | 19.9415 | [14 empty] | 0.015298 |  | 275.7978 |  |  |  | 73.9138 |  | 113.4313 |  | 136.3932 |  | 117.7596 |  | 152.6969
01/15 16:00:00 | 23.4581 | 25.0219 | 24.2585 | 24.4476 | 24.3891 | 24.9898 | 23.1562 | 33.9945 | 26.7559 | 28.5727 | 29.203 | 28.4493 | 29.9902 | 22.9005 | [14 empty] | 0.091141 |  | 123.0771 |  |  |  | 14.8642 |  | 32.174 |  | 39.7208 |  | 30.7889 |  | 50.2639
01/15 17:00:00 | 23.4861 | 25.0713 | 24.2925 | 24.4396 | 24.3898 | 25.0235 | 23.0187 | 33.9532 | 25.4679 | 27.9367 | 28.9905 | 28.177 | 29.6896 | 23.9488 | [14 empty] | 0.21848 |  | 100.088 |  |  |  | 2.3078 |  | 15.9035 |  | 25.4196 |  | 17.8783 |  | 32.957
01/15 18:00:00 | 23.4521 | 25.0604 | 24.2721 | 24.348 | 24.2993 | 24.9809 | 22.8067 | 33.2427 | 24.7231 | 27.2411 | 28.3556 | 27.6499 | 28.9149 | 26.3219 | [14 empty] | 0.41653 |  | 47.8964 |  |  |  | 2.5564 |  | 0.84494 |  | 4.1358 |  | 1.7636 |  | 6.7233
01/15 19:00:00 | 23.3212 | 24.8823 | 24.1347 | 24.0811 | 24.0444 | 24.7359 | 22.6411 | 31.375 | 23.8862 | 25.9433 | 26.9082 | 26.2186 | 27.4204 | 27.4025 | [14 empty] | 0.46246 |  | 15.7807 |  |  |  | 12.3644 |  | 2.1291 |  | 0.24426 |  | 1.4015 |  | 0.00032294
01/15 20:00:00 | 23.1624 | 24.6499 | 23.9682 | 23.755 | 23.7274 | 24.4245 | 22.4055 | 24.7973 | 17.6863 | 19.6639 | 20.8441 | 20.2611 | 21.2122 | 10.1972 | [14 empty] | 0.57278 |  | 213.1639 |  |  |  | 56.087 |  | 89.6189 |  | 113.3574 |  | 101.2824 |  | 121.3299
01/15 21:00:00 | 22.9869 | 24.4165 | 23.798 | 23.4628 | 23.3656 | 24.0924 | 21.9593 | 23.6135 | 17.1064 | 18.8852 | 19.936 | 19.414 | 20.2895 | 19.8594 | [14 empty] | 1.056 |  | 14.0931 |  |  |  | 7.5792 |  | 0.94905 |  | 0.0058657 |  | 0.1984 |  | 0.18499
01/15 22:00:00 | 22.7784 | 24.0982 | 23.5925 | 23.1007 | 22.923 | 23.6816 | 21.6746 | 22.2733 | 16.5245 | 18.0166 | 18.8868 | 18.4501 | 19.2577 | 22.4588 | [14 empty] | 1.2184 |  | 0.0344 |  |  |  | 35.2158 |  | 19.7336 |  | 12.7591 |  | 16.07 |  | 10.2472
01/15 23:00:00 | 22.544 | 23.6878 | 23.3594 | 22.6469 | 22.3929 | 23.2447 | 21.4372 | 22.7014 | 16.2709 | 18.0204 | 19.4233 | 18.9861 | 19.7667 | 23.1641 | [14 empty] | 1.2251 |  | 0.21408 |  |  |  | 47.5163 |  | 26.4584 |  | 13.9935 |  | 17.4557 |  | 11.5424
01/15 24:00:00 | 22.2846 | 23.3304 | 23.1015 | 22.2683 | 21.953 | 22.7872 | 21.2325 | 21.6131 | 15.883 | 17.4046 | 18.6012 | 18.2498 | 18.9656 | 25.9057 | [14 empty] | 1.1068 |  | 18.4262 |  |  |  | 100.454 |  | 72.2688 |  | 53.3559 |  | 58.6117 |  | 48.164
01/16 01:00:00 | 22.0031 | 22.973 | 22.8262 | 21.8796 | 21.5666 | 22.3999 | 21.1083 | 20.2141 | 15.273 | 16.5197 | 17.4308 | 17.1084 | 17.7869 | 25.4948 | [14 empty] | 0.80069 |  | 27.886 |  |  |  | 104.4853 |  | 80.5522 |  | 65.0284 |  | 70.3327 |  | 59.4129
01/16 02:00:00 | 21.7489 | 22.7097 | 22.5787 | 21.5934 | 21.2169 | 22.0547 | 21.0282 | 16.6981 | 14.7523 | 15.9576 | 16.918 | 16.6006 | 17.2252 | 25.9661 | [14 empty] | 0.51937 |  | 85.8967 |  |  |  | 125.7495 |  | 100.1707 |  | 81.8685 |  | 87.7134 |  | 76.403
01/16 03:00:00 | 21.5387 | 22.4825 | 22.3442 | 21.3369 | 20.8902 | 21.7955 | 20.9626 | 16.1385 | 14.255 | 15.3519 | 16.1951 | 15.9166 | 16.5123 | 26.5713 | [14 empty] | 0.33189 |  | 108.8439 |  |  |  | 151.691 |  | 125.8745 |  | 107.6658 |  | 113.5233 |  | 101.1831
01/16 04:00:00 | 21.3747 | 22.2474 | 22.1084 | 21.0709 | 20.6201 | 21.5399 | 20.8699 | 15.6798 | 13.8096 | 14.8213 | 15.6208 | 15.3906 | 15.9099 | 27.5368 | [14 empty] | 0.25484 |  | 140.5886 |  |  |  | 188.4376 |  | 161.6837 |  | 141.9929 |  | 147.5319 |  | 135.1858
01/16 05:00:00 | 21.1998 | 21.9977 | 21.8593 | 20.7856 | 20.344 | 21.2625 | 20.7703 | 18.0145 | 13.3852 | 14.4036 | 15.1832 | 34.4435 | 15.4611 | 28.359 | [14 empty] | 0.1845 |  | 107.009 |  |  |  | 224.2147 |  | 194.7528 |  | 173.6032 |  | 37.0205 |  | 166.3552
01/16 06:00:00 | 20.963 | 21.7229 | 21.5895 | 20.4748 | 20.1917 | 20.9538 | 20.6752 | 17.1399 | 13.0378 | 13.9296 | 32.9609 | 46.7744 | 14.9566 | 29.079 | [14 empty] | 0.082792 |  | 142.5423 |  |  |  | 257.3225 |  | 229.506 |  | 15.0687 |  | 313.126 |  | 199.4442
01/16 07:00:00 | 20.6417 | 21.4362 | 21.3076 | 20.3096 | 20.3897 | 20.631 | 20.6124 | 16.6819 | 12.7127 | 13.6064 | 45.742 | 47.1847 | 14.6362 | 29.6304 | [14 empty] | 0.0008603 |  | 167.6617 |  |  |  | 286.2084 |  | 256.7681 |  | 259.5855 |  | 308.1563 |  | 224.8257
01/16 08:00:00 | 20.3265 | 21.1414 | 21.0184 | 20.5133 | 20.7298 | 20.3025 | 20.9394 | 36.9039 | 37.2287 | 14.3081 | 61.4851 | 63.5807 | 42.6216 | 76.4452 | [14 empty] | 0.37563 |  | 1563.5152 |  |  |  | 1537.9334 |  | 3861.0236 |  | 223.8055 |  | 165.4953 |  | 1144.04
01/16 09:00:00 | 20.195 | 21.0152 | 20.8043 | 21.3947 | 22.1117 | 20.1871 | 22.0627 | 51.6612 | 53.6146 | 38.9072 | 57.3564 | 50.8069 | 61.2836 | 65.7394 | [14 empty] | 3.4884 |  | 198.197 |  |  |  | 147.0113 |  | 719.9686 |  | 70.2748 |  | 222.9792 |  | 19.8541
01/16 10:00:00 | 20.751 | 21.8483 | 20.9755 | 22.7072 | 23.2614 | 21.2495 | 22.9963 | 53.1884 | 42.3371 | 50.8932 | 49.075 | 45.6431 | 57.2807 | 27.4873 | [14 empty] | 5.0413 |  | 660.5511 |  |  |  | 220.5193 |  | 547.8374 |  | 466.0294 |  | 329.6343 |  | 887.6505
01/16 11:00:00 | 21.8404 | 23.5792 | 21.9107 | 23.7951 | 23.7565 | 23.208 | 23.0448 | 46.0497 | 34.9502 | 43.8607 | 42.7568 | 40.9863 | 44.5625 | 27.9521 | [14 empty] | 1.4507 |  | 327.5244 |  |  |  | 48.9732 |  | 253.0821 |  | 219.1796 |  | 169.8905 |  | 275.9053
01/16 12:00:00 | 22.7201 | 24.704 | 23.3206 | 24.3983 | 24.1079 | 24.4675 | 23.0433 | 42.0641 | 32.2921 | 37.8303 | 40.9437 | 38.8077 | 40.298 | 23.6864 | [14 empty] | 0.10447 |  | 337.7399 |  |  |  | 74.0572 |  | 200.0488 |  | 297.8144 |  | 228.6522 |  | 275.943
01/16 13:00:00 | 23.2723 | 25.143 | 24.2422 | 24.708 | 24.3944 | 24.9581 | 23.0877 | 38.0879 | 30.3329 | 34.2302 | 37.1399 | 34.8475 | 37.1802 | 21.3366 | [14 empty] | 0.034043 |  | 280.6057 |  |  |  | 80.9333 |  | 166.2454 |  | 249.7455 |  | 182.5443 |  | 251.0212
01/16 14:00:00 | 23.4275 | 25.2697 | 24.4501 | 24.7793 | 24.4854 | 25.0558 | 23.0201 | 35.6468 | 28.2529 | 31.9886 | 34.5856 | 32.4115 | 34.7673 | 20.602 | [14 empty] | 0.16594 |  | 226.3451 |  |  |  | 58.5361 |  | 129.6534 |  | 195.542 |  | 139.4652 |  | 200.6563
01/16 15:00:00 | 23.5335 | 25.3509 | 24.542 | 24.8632 | 24.5856 | 25.1278 | 22.9848 | 34.3218 | 26.5661 | 30.4884 | 33.0129 | 30.9234 | 33.2747 | 20.527 | [14 empty] | 0.30101 |  | 190.2982 |  |  |  | 36.4717 |  | 99.2299 |  | 155.8983 |  | 108.0857 |  | 162.5055
01/16 16:00:00 | 23.7651 | 25.6184 | 24.8439 | 25.1153 | 24.8458 | 25.3916 | 22.8814 | 27.215 | 25.0412 | 28.436 | 30.5102 | 28.6468 | 30.9775 | 22.2192 | [14 empty] | 0.78093 |  | 24.9577 |  |  |  | 7.9637 |  | 38.6489 |  | 68.7405 |  | 41.3136 |  | 76.7074
01/16 17:00:00 | 23.8748 | 25.816 | 25.0616 | 25.2719 | 25.0042 | 25.5711 | 22.6863 | 30.4057 | 23.645 | 26.6157 | 28.2584 | 26.5635 | 28.6771 | 42.3692 | [14 empty] | 1.4125 |  | 143.1255 |  |  |  | 350.5956 |  | 248.171 |  | 199.1141 |  | 249.82 |  | 187.4717
01/16 18:00:00 | 23.8582 | 25.805 | 25.0564 | 25.1871 | 24.9239 | 25.5345 | 22.8593 | 28.6832 | 22.4959 | 25.3619 | 26.9588 | 25.392 | 27.2837 | 14.6874 | [14 empty] | 0.99787 |  | 195.8826 |  |  |  | 60.9727 |  | 113.9439 |  | 150.5875 |  | 114.588 |  | 158.6666
01/16 19:00:00 | 23.7323 | 25.6195 | 24.903 | 24.9178 | 24.665 | 25.3043 | 22.7161 | 27.5708 | 21.5493 | 24.3099 | 25.8265 | 24.3241 | 26.0626 | 29.654 | [14 empty] | 1.0327 |  | 4.3397 |  |  |  | 65.6855 |  | 28.5593 |  | 14.6492 |  | 28.4074 |  | 12.8978
01/16 20:00:00 | 23.3774 | 25.1985 | 24.5357 | 24.4326 | 24.176 | 24.8334 | 22.759 | 25.796 | 20.5103 | 22.9189 | 24.1865 | 22.8309 | 24.4083 | 18.77 | [14 empty] | 0.38242 |  | 49.3651 |  |  |  | 3.0288 |  | 17.2138 |  | 29.3386 |  | 16.4914 |  | 31.7908
01/16 21:00:00 | 23.0166 | 24.8151 | 24.1718 | 24.0214 | 23.6636 | 24.3437 | 22.5853 | 20.0504 | 15.0088 | 17.0699 | 18.464 | 17.4289 | 18.6142 | 9.3363 | [14 empty] | 0.18607 |  | 114.7917 |  |  |  | 32.1767 |  | 59.8077 |  | 83.3141 |  | 65.4903 |  | 86.0787
01/16 22:00:00 | 22.7237 | 24.4928 | 23.884 | 23.6727 | 23.214 | 23.9139 | 22.3138 | 19.4879 | 14.582 | 13.904 | 18.0012 | 17.0016 | 18.1393 | 17.0994 | [14 empty] | 0.16798 |  | 5.7052 |  |  |  | 6.3371 |  | 10.21 |  | 0.81336 |  | 0.0095573 |  | 1.0815
01/16 23:00:00 | 22.4544 | 24.1337 | 23.6599 | 23.293 | 22.7635 | 23.489 | 22.1299 | 18.056 | 14.0375 | 16.1162 | 16.7489 | 15.8705 | 16.9048 | 17.8062 | [14 empty] | 0.10534 |  | 0.062388 |  |  |  | 14.2032 |  | 2.8561 |  | 1.1179 |  | 3.7468 |  | 0.81258
01/16 24:00:00 | 22.2043 | 23.7965 | 23.4713 | 22.8657 | 22.3571 | 23.1092 | 21.9993 | 16.7535 | 13.4133 | 14.8221 | 15.5454 | 14.7526 | 15.6849 | 18.4111 | [14 empty] | 0.042022 |  | 2.7477 |  |  |  | 24.9774 |  | 12.8809 |  | 8.2123 |  | 13.3843 |  | 7.4322
01/17 01:00:00 | 21.982 | 23.5255 | 23.233 | 22.5728 | 22.0755 | 22.8473 | 21.9146 | 13.7488 | 12.8946 | 11.9637 | 15.1992 | 14.4266 | 15.333 | 18.699 | [14 empty] | 0.0045411 |  | 24.5041 |  |  |  | 33.6904 |  | 45.3633 |  | 12.2484 |  | 18.2533 |  | 11.33
01/17 02:00:00 | 21.8245 | 23.2975 | 23.0693 | 22.35 | 21.8563 | 22.644 | 21.8944 | 13.2669 | 12.4546 | 11.7941 | 14.4579 | 13.7659 | 14.5767 | 18.5203 | [14 empty] | 0.004882 |  | 27.5982 |  |  |  | 36.7923 |  | 45.2415 |  | 16.5026 |  | 22.6044 |  | 15.5517
01/17 03:00:00 | 21.7056 | 23.0808 | 22.9483 | 22.1352 | 21.6395 | 22.4406 | 21.937 | 13.0954 | 10.4457 | 11.5897 | 14.0969 | 13.3997 | 14.2087 | 18.5717 | [14 empty] | 0.053548 |  | 29.9891 |  |  |  | 66.032 |  | 48.7486 |  | 20.0232 |  | 26.7496 |  | 19.0357
01/17 04:00:00 | 21.5883 | 22.9103 | 22.8301 | 21.9235 | 21.4209 | 22.2359 | 21.782 | 11.7477 | 10.2009 | 10.7466 | 11.2806 | 12.1727 | 12.9023 | 19.8154 | [14 empty] | 0.037543 |  | 65.0866 |  |  |  | 92.4388 |  | 82.2431 |  | 72.8422 |  | 58.411 |  | 47.791
01/17 05:00:00 | 21.4705 | 22.7896 | 22.7125 | 21.7562 | 21.2071 | 22.0386 | 21.686 | 11.528 | 9.8556 | 10.4533 | 11.1768 | 11.7408 | 12.4752 | 20.8883 | [14 empty] | 0.046426 |  | 87.6162 |  |  |  | 121.7199 |  | 108.8899 |  | 94.3126 |  | 83.6767 |  | 70.7808
01/17 06:00:00 | 21.346 | 22.6481 | 22.5848 | 21.6225 | 20.9702 | 21.8321 | 21.6545 | 11.3927 | 9.6354 | 10.2806 | 11.0241 | 10.4309 | 10.9215 | 19.8268 | [14 empty] | 0.095132 |  | 71.1355 |  |  |  | 103.8656 |  | 91.1316 |  | 77.4877 |  | 88.2839 |  | 79.3043
01/17 07:00:00 | 21.2238 | 22.5132 | 22.4602 | 21.4772 | 20.79 | 21.6541 | 21.6656 | 11.0779 | 9.3786 | 10.0047 | 10.7334 | 10.2793 | 10.7817 | 20.859 | [14 empty] | 0.19519 |  | 95.6704 |  |  |  | 131.8002 |  | 117.815 |  | 102.5284 |  | 111.9306 |  | 101.5526
01/17 08:00:00 | 21.1171 | 22.3893 | 22.3521 | 21.3519 | 20.6747 | 21.5436 | 21.9807 | 13.0147 | 12.2224 | 12.3069 | 12.6126 | 12.281 | 12.7474 | 65.3366 | [14 empty] | 0.74576 |  | 2737.5802 |  |  |  | 2821.1084 |  | 2812.1476 |  | 2779.8162 |  | 2814.8898 |  | 2765.6235
01/17 09:00:00 | 21.0354 | 22.2901 | 22.2601 | 21.25 | 20.5829 | 21.4554 | 22.9743 | 35.2448 | 12.8458 | 13.2439 | 40.948 | 44.0061 | 42.2481 | 20.9195 | [14 empty] | 3.7592 |  | 205.2154 |  |  |  | 65.1852 |  | 58.915 |  | 401.1415 |  | 532.9912 |  | 454.9083
01/17 10:00:00 | 21.3455 | 22.3001 | 22.3228 | 21.5663 | 20.9428 | 21.8044 | 23.2097 | 46.368 | 11.9025 | 14.101 | 53.7988 | 56.5899 | 38.4319 | 9.5971 | [14 empty] | 3.475 |  | 1352.0973 |  |  |  | 5.3146 |  | 20.2845 |  | 1953.7843 |  | 2208.3152 |  | 831.4442
01/17 11:00:00 | 22.4493 | 22.4866 | 22.647 | 23.1304 | 22.9113 | 23.422 | 23.3365 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1166 | [14 empty] | 0.78716 |  | 83.113 |  |  |  | 83.113 |  | 83.113 |  | 83.113 |  | 83.113 |  | 83.113
01/17 12:00:00 | 22.9111 | 22.6856 | 22.9136 | 24.0862 | 23.9102 | 24.1623 | 23.4841 | 0 | 0 | 0 | 0 | 0 | 0 | 1.336 | [14 empty] | 0.32832 |  | 1.7848 |  |  |  | 1.7848 |  | 1.7848 |  | 1.7848 |  | 1.7848 |  | 1.7848
01/17 13:00:00 | 22.8836 | 22.9907 | 23.187 | 24.1122 | 23.9357 | 24.224 | 23.4656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.33878 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/17 14:00:00 | 22.6725 | 23.043 | 23.1868 | 23.9207 | 23.727 | 24.0491 | 23.4706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.63701 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/17 15:00:00 | 22.5764 | 23.0597 | 23.1995 | 23.8299 | 23.6152 | 23.9526 | 23.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.5069 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/17 16:00:00 | 22.8967 | 23.52 | 23.6402 | 24.1323 | 23.8956 | 24.2754 | 23.9111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.029 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/17 17:00:00 | 23.1552 | 23.8774 | 23.9772 | 24.3659 | 24.113 | 24.5243 | 23.7699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.37788 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/17 18:00:00 | 23.1873 | 23.9451 | 24.0426 | 24.3848 | 24.1222 | 24.5526 | 23.3969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.043907 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/17 19:00:00 | 23.0638 | 23.8426 | 23.94 | 24.2101 | 23.9341 | 24.3839 | 23.1466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.0068556 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/17 20:00:00 | 22.7576 | 23.5534 | 23.6468 | 23.7904 | 23.4978 | 23.9693 | 22.8938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.018546 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/17 21:00:00 | 22.4002 | 23.2198 | 23.2936 | 23.3995 | 23.092 | 23.5789 | 22.6701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.072874 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/17 22:00:00 | 22.0854 | 22.9056 | 22.9838 | 23.0892 | 22.7679 | 23.2682 | 22.4301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.1188 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/17 23:00:00 | 21.8677 | 22.6775 | 22.7682 | 22.8105 | 22.4753 | 22.988 | 22.2731 | 0 | 0 | 0 | 0 | 0 | 0 | 13.4489 | [14 empty] | 0.16436 |  | 180.8742 |  |  |  | 180.8742 |  | 180.8742 |  | 180.8742 |  | 180.8742 |  | 180.8742
01/17 24:00:00 | 21.6783 | 22.4689 | 22.58 | 22.5606 | 22.2115 | 22.7364 | 22.3326 | 0 | 0 | 0 | 0 | 0 | 0 | 12.7576 | [14 empty] | 0.42809 |  | 162.7576 |  |  |  | 162.7576 |  | 162.7576 |  | 162.7576 |  | 162.7576 |  | 162.7576
01/18 01:00:00 | 21.4872 | 22.2565 | 22.3896 | 22.3264 | 21.9634 | 22.5003 | 22.3211 | 0 | 0 | 0 | 0 | 0 | 0 | 14.0104 | [14 empty] | 0.69545 |  | 196.2901 |  |  |  | 196.2901 |  | 196.2901 |  | 196.2901 |  | 196.2901 |  | 196.2901
01/18 02:00:00 | 21.3744 | 22.1292 | 22.2775 | 22.1674 | 21.7465 | 22.3395 | 22.2828 | 0 | 0 | 0 | 0 | 0 | 0 | 13.1343 | [14 empty] | 0.82513 |  | 172.5107 |  |  |  | 172.5107 |  | 172.5107 |  | 172.5107 |  | 172.5107 |  | 172.5107
01/18 03:00:00 | 21.2449 | 21.9342 | 22.1475 | 21.9953 | 21.5256 | 22.1671 | 22.2969 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9398 | [14 empty] | 1.1067 |  | 194.319 |  |  |  | 194.319 |  | 194.319 |  | 194.319 |  | 194.319 |  | 194.319
01/18 04:00:00 | 21.1113 | 21.7364 | 22.0128 | 21.8137 | 21.3008 | 21.9844 | 22.2354 | 39.0463 | 14.1355 | 14.986 | 43.7634 | 46.2336 | 34.9973 | 14.3968 | [14 empty] | 1.2635 |  | 607.5945 |  |  |  | 0.068264 |  | 0.34716 |  | 862.3934 |  | 1013.5797 |  | 424.3793
01/18 05:00:00 | 21.9123 | 21.6877 | 22.0156 | 22.5834 | 22.0308 | 22.2997 | 22.1296 | 28.4572 | 8.6219 | 8.0695 | 27.1531 | 26.7953 | 21.4271 | 14.3164 | [14 empty] | 0.047213 |  | 199.9621 |  |  |  | 32.4273 |  | 39.0242 |  | 164.7809 |  | 155.7235 |  | 50.5615
01/18 06:00:00 | 22.5371 | 21.6158 | 21.9427 | 23.0837 | 22.5432 | 22.5057 | 22.1008 | 27.2628 | 7.4744 | 8.148 | 22.7553 | 22.9302 | 18.0234 | 15.8952 | [14 empty] | 0.1903 |  | 129.2219 |  |  |  | 70.9104 |  | 60.0196 |  | 47.0613 |  | 49.4907 |  | 4.529
01/18 07:00:00 | 22.7496 | 21.5422 | 21.8738 | 23.1965 | 22.6739 | 22.5643 | 21.9478 | 25.5188 | 8.4824 | 9.4741 | 25.2298 | 24.8317 | 19.6607 | 17.1375 | [14 empty] | 0.64288 |  | 70.2456 |  |  |  | 74.9103 |  | 58.7286 |  | 65.485 |  | 59.2011 |  | 6.3664
01/18 08:00:00 | 22.8003 | 21.4123 | 21.7572 | 23.1974 | 22.6751 | 22.5525 | 22.2087 | 23.2886 | 9.333 | 9.3983 | 30.4184 | 31.1053 | 23.6536 | 65.8142 | [14 empty] | 0.34996 |  | 1808.4288 |  |  |  | 3190.1217 |  | 3182.7506 |  | 1252.8635 |  | 1204.7101 |  | 1777.5141
01/18 09:00:00 | 22.7642 | 21.2919 | 21.6464 | 23.2874 | 22.8444 | 22.5921 | 22.8208 | 28.2838 | 38.0771 | 34.8115 | 28.1126 | 27.8383 | 22.5923 | 9.3753 | [14 empty] | 0.0032067 |  | 357.5346 |  |  |  | 823.7943 |  | 647.0003 |  | 351.0884 |  | 340.8827 |  | 174.6896
01/18 10:00:00 | 22.8614 | 21.5411 | 21.8547 | 23.4418 | 23.0996 | 22.73 | 22.6803 | 25.7779 | 50.0362 | 37.0014 | 25.6973 | 25.3262 | 21.2596 | 19.2063 | [14 empty] | 0.032807 |  | 43.186 |  |  |  | 950.4829 |  | 316.6644 |  | 42.1326 |  | 37.4524 |  | 4.2159
01/18 11:00:00 | 23.0896 | 22.9764 | 22.8812 | 23.6952 | 23.4011 | 23.0334 | 22.6797 | 24.6326 | 32.9863 | 28.4211 | 24.3398 | 24.0205 | 19.2101 | 19.4053 | [14 empty] | 0.168 |  | 27.3248 |  |  |  | 184.4438 |  | 81.2852 |  | 24.3494 |  | 21.3007 |  | 0.038078
01/18 12:00:00 | 23.3467 | 24.9944 | 23.9066 | 23.96 | 23.6876 | 23.3147 | 22.7457 | 18.4685 | 27.9827 | 25.5031 | 19.4008 | 19.5654 | 17.5602 | 19.5693 | [14 empty] | 0.36122 |  | 1.2117 |  |  |  | 70.7863 |  | 35.2101 |  | 0.028388 |  | 1.4998e-05 |  | 4.0363
01/18 13:00:00 | 23.459 | 25.8769 | 24.3133 | 24.0876 | 23.8317 | 23.5066 | 22.6998 | 21.5068 | 27.0475 | 23.9195 | 20.93 | 20.5724 | 16.2555 | 21.3529 | [14 empty] | 0.57637 |  | 0.023677 |  |  |  | 32.4282 |  | 6.5876 |  | 0.17884 |  | 0.60917 |  | 25.9836
01/18 14:00:00 | 23.3566 | 25.8937 | 24.3081 | 23.9665 | 23.7241 | 23.4047 | 22.646 | 16.5368 | 25.5923 | 19.2242 | 17.1439 | 17.2028 | 13.8511 | 21.8046 | [14 empty] | 0.50487 |  | 27.7502 |  |  |  | 14.3464 |  | 6.6584 |  | 21.7221 |  | 21.1761 |  | 63.2573
01/18 15:00:00 | 23.2832 | 25.8791 | 24.2811 | 23.8908 | 23.6609 | 23.3326 | 22.5896 | 20.4544 | 24.4628 | 22.5379 | 19.73 | 19.2561 | 15.8349 | 21.5186 | [14 empty] | 0.48112 |  | 1.1325 |  |  |  | 8.6684 |  | 1.0389 |  | 3.1991 |  | 5.119 |  | 32.3047
01/18 16:00:00 | 23.4438 | 26.0091 | 24.4909 | 24.0212 | 23.7927 | 23.4737 | 22.5966 | 16.348 | 23.4222 | 18.0113 | 16.6796 | 18.0684 | 13.62 | 22.0836 | [14 empty] | 0.71781 |  | 32.8965 |  |  |  | 1.7918 |  | 16.5837 |  | 29.2035 |  | 16.1217 |  | 71.6319
01/18 17:00:00 | 23.5138 | 26.1203 | 24.6064 | 24.0743 | 23.8529 | 23.5425 | 22.6457 | 18.1929 | 22.1179 | 20.1806 | 17.4865 | 16.6956 | 13.9722 | 21.1554 | [14 empty] | 0.75362 |  | 8.7769 |  |  |  | 0.92623 |  | 0.95032 |  | 13.4615 |  | 19.89 |  | 51.5989
01/18 18:00:00 | 23.4371 | 26.0897 | 24.5598 | 23.9727 | 23.7427 | 23.4325 | 22.5688 | 16.6892 | 20.8337 | 18.495 | 16.0132 | 15.5496 | 12.8398 | 22.4899 | [14 empty] | 0.75392 |  | 33.6482 |  |  |  | 2.7431 |  | 15.9587 |  | 41.9479 |  | 48.1679 |  | 93.1241
01/18 19:00:00 | 23.2596 | 25.9497 | 24.4199 | 23.7693 | 23.5167 | 23.2315 | 22.5294 | 16.6764 | 19.9437 | 18.0047 | 15.8171 | 15.4648 | 12.8001 | 22.5589 | [14 empty] | 0.5332 |  | 34.6034 |  |  |  | 6.8393 |  | 20.7408 |  | 45.4517 |  | 50.3266 |  | 95.2347
01/18 20:00:00 | 22.8567 | 25.6484 | 24.0571 | 23.3428 | 23.0618 | 22.8069 | 22.5616 | 17.0674 | 19.4295 | 17.8979 | 16.1728 | 15.866 | 13.2506 | 43.2912 | [14 empty] | 0.087098 |  | 687.6884 |  |  |  | 569.3799 |  | 644.8197 |  | 735.4071 |  | 752.1407 |  | 902.4376
01/18 21:00:00 | 22.4468 | 25.2884 | 23.6786 | 22.9064 | 22.5965 | 22.3722 | 22.8753 | 13.5592 | 14.3578 | 13.6224 | 12.6311 | 12.312 | 10.5221 | 4.9549 | [14 empty] | 0.18361 |  | 74.0331 |  |  |  | 88.414 |  | 75.1245 |  | 58.9227 |  | 54.1259 |  | 30.9934
01/18 22:00:00 | 22.1089 | 24.9366 | 23.3703 | 22.5499 | 22.2122 | 22.0167 | 22.5325 | 10.9474 | 13.9508 | 10.9799 | 10.7664 | 11.7447 | 9.168 | 12.5324 | [14 empty] | 0.17948 |  | 2.5123 |  |  |  | 2.0119 |  | 2.4102 |  | 3.1188 |  | 0.62046 |  | 11.3189
01/18 23:00:00 | 21.8526 | 24.595 | 23.1333 | 22.2778 | 21.8439 | 21.7578 | 22.2114 | 12.9256 | 13.5753 | 13.1294 | 12.0405 | 11.5596 | 10.1095 | 16.7271 | [14 empty] | 0.12878 |  | 14.4507 |  |  |  | 9.9336 |  | 12.9429 |  | 21.9634 |  | 26.7026 |  | 43.7918
01/18 24:00:00 | 21.6276 | 24.2675 | 22.9253 | 22.0287 | 21.4576 | 21.5174 | 21.9981 | 12.2144 | 13.1649 | 12.353 | 11.4088 | 11.1342 | 9.6167 | 18.5966 | [14 empty] | 0.1373 |  | 40.7333 |  |  |  | 29.504 |  | 38.9828 |  | 51.6654 |  | 55.6873 |  | 80.6385
01/19 01:00:00 | 21.3298 | 23.9521 | 22.6479 | 21.6996 | 21.1016 | 21.1997 | 21.8544 | 11.7907 | 12.702 | 10.0729 | 9.9095 | 10.8013 | 8.4553 | 19.6058 | [14 empty] | 0.27521 |  | 61.0761 |  |  |  | 47.663 |  | 90.8773 |  | 94.0183 |  | 77.5198 |  | 124.3337
01/19 02:00:00 | 21.082 | 23.674 | 22.4468 | 21.4756 | 20.8307 | 20.9849 | 21.7609 | 9.6603 | 12.2899 | 9.9283 | 9.676 | 9.4936 | 8.2718 | 19.4091 | [14 empty] | 0.46085 |  | 95.0393 |  |  |  | 50.6825 |  | 89.8864 |  | 94.7324 |  | 98.3173 |  | 124.0391
01/19 03:00:00 | 20.8936 | 23.4143 | 22.3038 | 21.317 | 20.6327 | 20.8351 | 21.7495 | 9.2251 | 10.2369 | 9.5521 | 9.1952 | 9.0914 | 7.8116 | 18.9899 | [14 empty] | 0.73266 |  | 95.3515 |  |  |  | 76.6144 |  | 89.0723 |  | 95.9356 |  | 97.9801 |  | 124.9547
01/19 04:00:00 | 20.7589 | 23.2146 | 22.1639 | 21.162 | 20.49 | 20.6891 | 21.6848 | 8.8962 | 10.0742 | 9.2256 | 8.8411 | 8.7545 | 7.5296 | 19.8056 | [14 empty] | 0.85714 |  | 119.014 |  |  |  | 94.6993 |  | 111.9357 |  | 120.2193 |  | 122.1264 |  | 150.7002
01/19 05:00:00 | 20.6233 | 23.0582 | 22.0218 | 21.0024 | 20.3441 | 20.5388 | 21.6156 | 8.6146 | 9.8339 | 8.9612 | 8.5684 | 21.3844 | 7.3126 | 20.5586 | [14 empty] | 0.98464 |  | 142.6582 |  |  |  | 115.0192 |  | 134.4989 |  | 143.7628 |  | 0.68197 |  | 175.4545
01/19 06:00:00 | 20.4799 | 22.905 | 21.878 | 20.8411 | 20.3194 | 20.3865 | 21.5783 | 8.2818 | 9.5451 | 8.6555 | 8.232 | 44.2585 | 6.9923 | 20.2948 | [14 empty] | 1.2066 |  | 144.3136 |  |  |  | 115.5576 |  | 135.4728 |  | 145.5116 |  | 574.2591 |  | 176.9579
01/19 07:00:00 | 20.3428 | 22.7517 | 21.7387 | 20.6841 | 20.6195 | 20.2391 | 21.5484 | 17.4512 | 9.3064 | 8.4984 | 8.1103 | 32.7141 | 19.757 | 21.4833 | [14 empty] | 1.4534 |  | 16.2579 |  |  |  | 148.2759 |  | 168.6075 |  | 178.8365 |  | 126.1305 |  | 2.98
01/19 08:00:00 | 20.3125 | 22.5965 | 21.5995 | 20.5271 | 21.0684 | 20.2149 | 21.8592 | 47.4269 | 12.3318 | 10.917 | 9.9721 | 55.2364 | 60.566 | 74.4733 | [14 empty] | 2.3923 |  | 731.5114 |  |  |  | 3861.5733 |  | 4039.4034 |  | 4160.4099 |  | 370.06 |  | 193.414
01/19 09:00:00 | 20.6617 | 22.4534 | 21.4769 | 20.3849 | 21.9557 | 20.986 | 22.8264 | 51.1912 | 14.2935 | 36.4434 | 41.8222 | 45.2396 | 56.7001 | 22.2033 | [14 empty] | 4.686 |  | 840.3003 |  |  |  | 62.5655 |  | 202.7793 |  | 384.903 |  | 530.6694 |  | 1190.0292
01/19 10:00:00 | 21.5308 | 22.3787 | 21.6939 | 20.5822 | 23.27 | 22.7375 | 22.8585 | 51.2407 | 24.328 | 49.044 | 57.3044 | 38.6022 | 43.6123 | 19.0812 | [14 empty] | 1.7626 |  | 1034.2367 |  |  |  | 27.5291 |  | 897.7726 |  | 1461.0113 |  | 381.0711 |  | 601.7738
01/19 11:00:00 | 22.7718 | 22.5134 | 22.7072 | 22.0005 | 24.0371 | 24.3818 | 22.7773 | 45.7609 | 34.5489 | 37.9721 | 43.6822 | 36.1713 | 38.8119 | 21.4904 | [14 empty] | 3.0538e-05 |  | 589.0578 |  |  |  | 170.5249 |  | 271.6476 |  | 492.4751 |  | 215.5282 |  | 300.0363
01/19 12:00:00 | 23.6313 | 23.0381 | 24.0905 | 23.9417 | 24.3996 | 25.0428 | 22.9471 | 41.4459 | 26.1413 | 32.9818 | 36.6649 | 33.5451 | 36.7325 | 18.2204 | [14 empty] | 0.4682 |  | 539.426 |  |  |  | 62.7413 |  | 217.9011 |  | 340.2022 |  | 234.8488 |  | 342.6973
01/19 13:00:00 | 24.0477 | 23.8826 | 24.7912 | 24.7698 | 24.6369 | 25.2644 | 23.0293 | 39.5816 | 22.0759 | 31.252 | 34.6688 | 31.6725 | 35.0532 | 17.2436 | [14 empty] | 1.037 |  | 498.9856 |  |  |  | 23.3511 |  | 196.2367 |  | 303.6374 |  | 208.1935 |  | 317.1823
01/19 14:00:00 | 24.114 | 24.2089 | 24.8745 | 24.7354 | 24.6186 | 25.2576 | 23.1199 | 36.5495 | 20.9514 | 28.9813 | 31.9986 | 29.1007 | 32.0355 | 16.9285 | [14 empty] | 0.98821 |  | 384.9849 |  |  |  | 16.184 |  | 145.2705 |  | 227.1077 |  | 148.1623 |  | 228.222
01/19 15:00:00 | 24.24 | 24.2984 | 24.9174 | 24.7062 | 24.6447 | 25.325 | 23.2821 | 33.1721 | 19.3428 | 26.5678 | 28.8605 | 26.1522 | 28.8347 | 12.6735 | [14 empty] | 0.91744 |  | 420.1933 |  |  |  | 44.4798 |  | 193.0495 |  | 262.0194 |  | 181.6747 |  | 261.1834
01/19 16:00:00 | 24.5812 | 24.6258 | 25.237 | 24.9514 | 24.9114 | 25.625 | 23.4057 | 31.0024 | 17.6623 | 24.4729 | 26.7166 | 24.2169 | 26.62 | 5.0486 | [14 empty] | 1.3818 |  | 673.5993 |  |  |  | 159.1032 |  | 377.3036 |  | 469.4997 |  | 367.4214 |  | 465.3237
01/19 17:00:00 | 24.9016 | 25.0168 | 25.6049 | 25.2091 | 25.1834 | 25.9233 | 23.2859 | 28.9739 | 16.7542 | 23.0171 | 25.0052 | 22.6919 | 25.0501 | 17.4197 | [14 empty] | 2.6105 |  | 133.5001 |  |  |  | 0.44286 |  | 31.3312 |  | 57.5401 |  | 27.7958 |  | 58.2231
01/19 18:00:00 | 24.9556 | 25.1555 | 25.7023 | 25.2183 | 25.1935 | 25.9685 | 23.0178 | 28.4594 | 16.4212 | 22.5305 | 24.6138 | 22.453 | 24.8031 | 18.344 | [14 empty] | 3.7552 |  | 102.3209 |  |  |  | 3.6973 |  | 17.5261 |  | 39.3094 |  | 16.8832 |  | 41.7193
01/19 19:00:00 | 24.8327 | 25.0361 | 25.5757 | 25.0352 | 24.9785 | 25.7828 | 22.7972 | 25.8735 | 15.7084 | 20.9827 | 22.2433 | 20.3599 | 22.3817 | 22.132 | [14 empty] | 4.1433 |  | 13.9985 |  |  |  | 41.2635 |  | 1.3211 |  | 0.012382 |  | 3.1406 |  | 0.062329
01/19 20:00:00 | 24.4767 | 24.7332 | 25.2142 | 24.5981 | 24.5169 | 25.3484 | 22.6297 | 26.0127 | 15.333 | 20.6907 | 22.4526 | 20.6643 | 22.6254 | 23.7605 | [14 empty] | 3.4116 |  | 5.0724 |  |  |  | 71.0239 |  | 9.4238 |  | 1.7107 |  | 9.5867 |  | 1.2886
01/19 21:00:00 | 24.0666 | 24.3701 | 24.8111 | 24.0813 | 23.9727 | 24.8226 | 22.4046 | 21.224 | 11.5269 | 16.06 | 17.9731 | 16.5819 | 18.127 | 11.6913 | [14 empty] | 2.7622 |  | 90.8716 |  |  |  | 0.027042 |  | 19.0852 |  | 39.4613 |  | 23.9176 |  | 41.4183
01/19 22:00:00 | 23.7079 | 24.0044 | 24.4603 | 23.5904 | 23.449 | 24.319 | 22.0785 | 20.4063 | 11.293 | 15.5863 | 17.3923 | 16.1035 | 17.5381 | 17.2223 | [14 empty] | 2.6549 |  | 10.1379 |  |  |  | 35.1563 |  | 2.6765 |  | 0.028896 |  | 1.2519 |  | 0.099735
01/19 23:00:00 | 23.3673 | 23.6317 | 24.1312 | 23.1412 | 22.9626 | 23.8515 | 21.9246 | 19.9922 | 11.1757 | 15.2613 | 17.066 | 15.8464 | 17.2095 | 19.3889 | [14 empty] | 2.0816 |  | 0.36394 |  |  |  | 67.4569 |  | 17.0372 |  | 5.3961 |  | 12.5495 |  | 4.75
01/19 24:00:00 | 23.0023 | 23.288 | 23.7737 | 22.7221 | 22.5077 | 23.4085 | 21.745 | 17.9283 | 10.6445 | 14.1576 | 15.3456 | 14.2835 | 15.4992 | 20.1486 | [14 empty] | 1.581 |  | 4.9295 |  |  |  | 90.3279 |  | 35.8923 |  | 23.0691 |  | 34.3989 |  | 21.6165
01/20 01:00:00 | 22.6746 | 22.9469 | 23.451 | 22.4088 | 22.169 | 23.0772 | 21.6388 | 16.3666 | 8.7839 | 10.9943 | 13.9954 | 12.9948 | 14.1279 | 20.784 | [14 empty] | 1.0729 |  | 19.514 |  |  |  | 144.0026 |  | 95.8388 |  | 46.0848 |  | 60.6724 |  | 44.3041
01/20 02:00:00 | 22.4334 | 22.7172 | 23.2449 | 22.1611 | 21.8987 | 22.8142 | 21.5606 | 14.0457 | 10.1948 | 13.4228 | 14.1913 | 13.2384 | 14.3443 | 21.761 | [14 empty] | 0.7618 |  | 59.5256 |  |  |  | 133.7754 |  | 69.5248 |  | 57.2992 |  | 72.6338 |  | 55.0076
01/20 03:00:00 | 22.2356 | 22.5018 | 23.0642 | 21.9142 | 21.6315 | 22.5525 | 21.5643 | 13.6552 | 8.4765 | 10.8164 | 13.6793 | 12.7798 | 13.809 | 21.1479 | [14 empty] | 0.45063 |  | 56.1398 |  |  |  | 160.5635 |  | 106.7391 |  | 55.7801 |  | 70.0243 |  | 53.8594
01/20 04:00:00 | 22.0873 | 22.2791 | 22.8644 | 21.6694 | 21.365 | 22.2912 | 21.4929 | 13.4211 | 8.4388 | 10.76 | 13.329 | 12.4546 | 13.4595 | 21.6653 | [14 empty] | 0.35323 |  | 67.9671 |  |  |  | 174.9406 |  | 118.9253 |  | 69.4949 |  | 84.8383 |  | 67.3361
01/20 05:00:00 | 21.9345 | 22.1204 | 22.7155 | 21.4237 | 21.0905 | 22.0285 | 21.4624 | 11.9536 | 8.0972 | 9.9131 | 10.6245 | 10.1247 | 10.8201 | 22.3986 | [14 empty] | 0.2229 |  | 109.0987 |  |  |  | 204.5308 |  | 155.8881 |  | 138.631 |  | 150.6502 |  | 134.0633
01/20 06:00:00 | 21.7867 | 21.9732 | 22.5672 | 21.2294 | 20.8863 | 21.8231 | 21.441 | 12.7427 | 7.9913 | 10.1752 | 12.6962 | 11.8708 | 12.8152 | 21.7895 | [14 empty] | 0.11952 |  | 81.8448 |  |  |  | 190.3918 |  | 134.8935 |  | 82.6896 |  | 98.3821 |  | 80.5394
01/20 07:00:00 | 21.6345 | 21.8199 | 22.4196 | 21.0474 | 20.6885 | 21.6286 | 21.4081 | 12.7987 | 7.8644 | 10.1865 | 11.3763 | 10.8654 | 11.5768 | 22.139 | [14 empty] | 0.051268 |  | 87.242 |  |  |  | 203.7645 |  | 142.8614 |  | 115.8358 |  | 127.0931 |  | 111.5609
01/20 08:00:00 | 21.4847 | 21.6691 | 22.2742 | 20.8529 | 20.4813 | 21.4213 | 21.6969 | 15.02 | 10.1009 | 12.5282 | 13.416 | 12.8828 | 13.672 | 74.0794 | [14 empty] | 0.045065 |  | 3488.003 |  |  |  | 4093.2403 |  | 3788.5441 |  | 3680.0408 |  | 3745.0215 |  | 3649.0532
01/20 09:00:00 | 21.3586 | 21.5402 | 22.1552 | 20.7377 | 20.3595 | 21.2972 | 22.6971 | 38.1403 | 38.7464 | 15.2814 | 43.6256 | 46.452 | 44.8568 | 38.7313 | [14 empty] | 1.7916 |  | 0.34928 |  |  |  | 0.00022795 |  | 549.8975 |  | 23.9543 |  | 59.6103 |  | 37.5221
01/20 10:00:00 | 21.5522 | 21.7237 | 22.1391 | 20.9857 | 20.6239 | 21.5411 | 23.0005 | 52.7848 | 39.8729 | 29.0283 | 60.916 | 63.5853 | 61.1878 | 10.0546 | [14 empty] | 2.0977 |  | 1825.872 |  |  |  | 889.1288 |  | 359.9997 |  | 2586.8793 |  | 2865.5318 |  | 2614.601
01/20 11:00:00 | 22.4421 | 22.7935 | 22.4591 | 22.4248 | 22.2443 | 22.971 | 22.7308 | 40.5514 | 28.5375 | 32.9883 | 41.717 | 42.3548 | 39.6056 | 18.1071 | [14 empty] | 0.083348 |  | 503.7476 |  |  |  | 108.7938 |  | 221.451 |  | 557.4264 |  | 587.9526 |  | 462.1879
01/20 12:00:00 | 23.5951 | 23.9436 | 23.171 | 24.4216 | 24.317 | 24.9012 | 22.8031 | 35.5218 | 24.9499 | 26.8704 | 35.7174 | 35.1917 | 33.8078 | 16.2754 | [14 empty] | 0.62729 |  | 370.4249 |  |  |  | 75.2467 |  | 112.2553 |  | 377.9913 |  | 357.828 |  | 307.3879
01/20 13:00:00 | 24.1488 | 24.5614 | 23.7364 | 25.238 | 25.117 | 25.6419 | 22.9553 | 32.5191 | 23.3599 | 23.1122 | 32.8342 | 32.5559 | 31.6729 | 14.3159 | [14 empty] | 1.4244 |  | 331.3556 |  |  |  | 81.7943 |  | 77.3742 |  | 342.9281 |  | 332.698 |  | 301.2659
01/20 14:00:00 | 24.303 | 24.7617 | 23.9247 | 25.2636 | 25.159 | 25.6631 | 23.1535 | 30.0172 | 21.5601 | 21.5443 | 30.1583 | 30.0199 | 28.9806 | 12.4839 | [14 empty] | 1.3212 |  | 307.4182 |  |  |  | 82.3773 |  | 82.0922 |  | 312.3854 |  | 307.5114 |  | 272.1421
01/20 15:00:00 | 24.4714 | 24.9671 | 24.2089 | 25.3613 | 25.2713 | 25.7752 | 23.432 | 0 | 0 | 0 | 0 | 0 | 0 | 7.789 | [14 empty] | 1.0804 |  | 60.6693 |  |  |  | 60.6693 |  | 60.6693 |  | 60.6693 |  | 60.6693 |  | 60.6693
01/20 16:00:00 | 24.4527 | 25.1415 | 24.399 | 25.3671 | 25.3105 | 25.8104 | 23.613 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0739 | [14 empty] | 0.70511 |  | 9.4492 |  |  |  | 9.4492 |  | 9.4492 |  | 9.4492 |  | 9.4492 |  | 9.4492
01/20 17:00:00 | 24.3308 | 25.2058 | 24.4757 | 25.2638 | 25.2243 | 25.7329 | 23.5749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.57138 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/20 18:00:00 | 24.1371 | 25.1233 | 24.4001 | 25.0634 | 25.0246 | 25.5454 | 23.2331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.81728 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/20 19:00:00 | 23.8759 | 24.9334 | 24.2199 | 24.7841 | 24.6923 | 25.2705 | 22.945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.86649 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/20 20:00:00 | 23.4125 | 24.5908 | 23.8212 | 24.3034 | 24.142 | 24.7896 | 22.702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.50484 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/20 21:00:00 | 22.9792 | 24.2169 | 23.4354 | 23.851 | 23.705 | 24.3334 | 22.4731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.25618 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/20 22:00:00 | 22.656 | 23.8769 | 23.2013 | 23.5057 | 23.3603 | 23.9811 | 22.3492 | 0 | 0 | 0 | 0 | 0 | 0 | 14.2526 | [14 empty] | 0.09411 |  | 203.1379 |  |  |  | 203.1379 |  | 203.1379 |  | 203.1379 |  | 203.1379 |  | 203.1379
01/20 23:00:00 | 22.4371 | 23.634 | 23.0534 | 23.1993 | 23.0483 | 23.6659 | 22.4132 | 0 | 0 | 0 | 0 | 0 | 0 | 13.2204 | [14 empty] | 0.00057342 |  | 174.7785 |  |  |  | 174.7785 |  | 174.7785 |  | 174.7785 |  | 174.7785 |  | 174.7785
01/20 24:00:00 | 22.2365 | 23.4082 | 22.8537 | 22.9159 | 22.7551 | 23.3722 | 22.4737 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6708 | [14 empty] | 0.056277 |  | 186.8897 |  |  |  | 186.8897 |  | 186.8897 |  | 186.8897 |  | 186.8897 |  | 186.8897
01/21 01:00:00 | 21.978 | 23.18 | 22.6535 | 22.6492 | 22.4759 | 23.0946 | 22.4628 | 0 | 0 | 0 | 0 | 0 | 0 | 11.8414 | [14 empty] | 0.235 |  | 140.2177 |  |  |  | 140.2177 |  | 140.2177 |  | 140.2177 |  | 140.2177 |  | 140.2177
01/21 02:00:00 | 21.7923 | 23.0236 | 22.5161 | 22.4502 | 22.2083 | 22.8298 | 22.3893 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5701 | [14 empty] | 0.35635 |  | 212.2874 |  |  |  | 212.2874 |  | 212.2874 |  | 212.2874 |  | 212.2874 |  | 212.2874
01/21 03:00:00 | 21.6459 | 22.8548 | 22.3634 | 22.2329 | 21.9258 | 22.5519 | 22.3122 | 31.1838 | 26.5079 | 23.7871 | 34.7327 | 36.8048 | 35.0656 | 14.831 | [14 empty] | 0.44397 |  | 267.4152 |  |  |  | 136.3491 |  | 80.2126 |  | 396.0786 |  | 482.849 |  | 409.4374
01/21 04:00:00 | 21.8992 | 22.8751 | 22.4358 | 22.3162 | 22.0086 | 22.6346 | 22.2437 | 24.7132 | 16.504 | 14.2368 | 24.003 | 24.0005 | 23.536 | 14.531 | [14 empty] | 0.11867 |  | 103.6783 |  |  |  | 3.8929 |  | 0.086562 |  | 89.7189 |  | 89.6718 |  | 81.0907
01/21 05:00:00 | 22.0733 | 22.8441 | 22.4302 | 22.4275 | 22.1153 | 22.7395 | 22.1996 | 19.9189 | 15.2933 | 16.7486 | 22.5936 | 22.3908 | 22.0717 | 15.1577 | [14 empty] | 0.015951 |  | 22.6691 |  |  |  | 0.018393 |  | 2.5309 |  | 55.2931 |  | 52.3174 |  | 47.803
01/21 06:00:00 | 22.0876 | 22.7736 | 22.3872 | 22.4441 | 22.1247 | 22.7499 | 22.1868 | 19.3274 | 12.7232 | 13.2468 | 21.5702 | 21.381 | 21.0801 | 16.3554 | [14 empty] | 0.0098507 |  | 8.8325 |  |  |  | 13.193 |  | 9.6637 |  | 27.1939 |  | 25.2562 |  | 22.3225
01/21 07:00:00 | 22.0582 | 22.6911 | 22.3148 | 22.4059 | 22.0775 | 22.7056 | 22.1654 | 18.3337 | 12.5214 | 12.8982 | 18.0059 | 18.186 | 17.7572 | 15.7045 | [14 empty] | 0.011488 |  | 6.9123 |  |  |  | 10.1325 |  | 7.8752 |  | 5.2964 |  | 6.1579 |  | 4.2134
01/21 08:00:00 | 22.0246 | 22.6288 | 22.258 | 22.3469 | 22.0143 | 22.6437 | 22.1465 | 17.7377 | 12.1531 | 12.5152 | 17.6145 | 17.6958 | 17.3484 | 15.3973 | [14 empty] | 0.014855 |  | 5.4776 |  |  |  | 10.5244 |  | 8.3064 |  | 4.9162 |  | 5.2834 |  | 3.8069
01/21 09:00:00 | 21.9753 | 22.5533 | 22.1881 | 22.2793 | 21.9436 | 22.5728 | 22.602 | 20.6242 | 15.8513 | 15.3969 | 21.4234 | 24.3527 | 23.465 | 48.2202 | [14 empty] | 0.39266 |  | 761.541 |  |  |  | 1047.7465 |  | 1077.3691 |  | 718.0711 |  | 569.6601 |  | 612.8239
01/21 10:00:00 | 21.9199 | 22.4782 | 22.1151 | 22.2087 | 21.8722 | 22.5033 | 23.6384 | 21.7885 | 16.4436 | 16.2257 | 21.2747 | 22.5572 | 20.2579 | 4.1533 | [14 empty] | 2.9533 |  | 311.0004 |  |  |  | 151.0516 |  | 145.7429 |  | 293.1423 |  | 338.7063 |  | 259.3596
01/21 11:00:00 | 21.9233 | 22.4292 | 22.0954 | 22.1797 | 21.8401 | 22.4647 | 24.0507 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4662 | [14 empty] | 4.5255 |  | 2.1497 |  |  |  | 2.1497 |  | 2.1497 |  | 2.1497 |  | 2.1497 |  | 2.1497
01/21 12:00:00 | 21.6604 | 22.2856 | 21.9732 | 21.9773 | 21.7543 | 22.3569 | 24.3345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 7.1509 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/21 13:00:00 | 21.5618 | 22.2879 | 22.0062 | 21.9257 | 21.7807 | 22.3997 | 24.5818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 9.1201 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/21 14:00:00 | 21.6563 | 22.4244 | 22.1742 | 22.0297 | 21.9166 | 22.561 | 24.7879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 9.8072 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/21 15:00:00 | 21.7694 | 22.5468 | 22.3233 | 22.1437 | 22.0468 | 22.7077 | 24.9368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 10.0326 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/21 16:00:00 | 21.8685 | 22.6451 | 22.4464 | 22.243 | 22.1505 | 22.8216 | 24.9935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 9.7655 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/21 17:00:00 | 21.939 | 22.7188 | 22.5345 | 22.3135 | 22.225 | 22.9034 | 24.906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 8.8032 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/21 18:00:00 | 22.0006 | 22.7864 | 22.6109 | 22.374 | 22.2903 | 22.9752 | 24.6375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 6.953 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/21 19:00:00 | 22.0119 | 22.8143 | 22.6387 | 22.3776 | 22.2955 | 22.9814 | 24.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 5.5797 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/21 20:00:00 | 21.9685 | 22.7598 | 22.5916 | 22.3083 | 22.2254 | 22.893 | 24.1165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.6139 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/21 21:00:00 | 21.8802 | 22.6594 | 22.4975 | 22.1974 | 22.1138 | 22.7672 | 23.7995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.6835 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/21 22:00:00 | 21.7741 | 22.5539 | 22.391 | 22.0765 | 21.9913 | 22.6417 | 23.5936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.3108 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/21 23:00:00 | 21.6378 | 22.4162 | 22.2524 | 21.9236 | 21.8356 | 22.4823 | 23.3975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.0963 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/21 24:00:00 | 21.4933 | 22.2646 | 22.1041 | 21.7611 | 21.6697 | 22.3119 | 23.2059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.933 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/22 01:00:00 | 21.3786 | 22.1062 | 21.9859 | 21.632 | 21.5374 | 22.1376 | 23.0776 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6549 | [14 empty] | 2.8867 |  | 160.1477 |  |  |  | 160.1477 |  | 160.1477 |  | 160.1477 |  | 160.1477 |  | 160.1477
01/22 02:00:00 | 21.2906 | 21.9805 | 21.8946 | 21.5327 | 21.4352 | 22.0008 | 23.059 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0907 | [14 empty] | 3.1272 |  | 82.6413 |  |  |  | 82.6413 |  | 82.6413 |  | 82.6413 |  | 82.6413 |  | 82.6413
01/22 03:00:00 | 21.1885 | 21.8402 | 21.7509 | 21.4183 | 21.2736 | 21.8479 | 23.0079 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5011 | [14 empty] | 3.3101 |  | 90.2712 |  |  |  | 90.2712 |  | 90.2712 |  | 90.2712 |  | 90.2712 |  | 90.2712
01/22 04:00:00 | 21.0781 | 21.6901 | 21.5989 | 21.2945 | 21.0547 | 21.6839 | 22.912 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2781 | [14 empty] | 3.3634 |  | 105.6391 |  |  |  | 105.6391 |  | 105.6391 |  | 105.6391 |  | 105.6391 |  | 105.6391
01/22 05:00:00 | 20.959 | 21.5332 | 21.4817 | 21.1611 | 20.8361 | 21.5138 | 22.8767 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9451 | [14 empty] | 3.6776 |  | 98.9054 |  |  |  | 98.9054 |  | 98.9054 |  | 98.9054 |  | 98.9054 |  | 98.9054
01/22 06:00:00 | 20.8302 | 21.3652 | 21.3556 | 21.0173 | 20.613 | 21.2799 | 22.8441 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6237 | [14 empty] | 4.056 |  | 112.8635 |  |  |  | 112.8635 |  | 112.8635 |  | 112.8635 |  | 112.8635 |  | 112.8635
01/22 07:00:00 | 20.7054 | 21.2472 | 21.2321 | 20.8777 | 20.4494 | 21.1117 | 22.7774 | 0 | 0 | 0 | 0 | 0 | 0 | 11.3329 | [14 empty] | 4.2931 |  | 128.4346 |  |  |  | 128.4346 |  | 128.4346 |  | 128.4346 |  | 128.4346 |  | 128.4346
01/22 08:00:00 | 20.5818 | 21.1295 | 21.1092 | 20.7392 | 20.3338 | 20.9954 | 22.692 | 21.4513 | 17.3572 | 17.3529 | 23.5233 | 44.0149 | 23.9842 | 12.1284 | [14 empty] | 4.4533 |  | 86.9175 |  |  |  | 27.34 |  | 27.2956 |  | 129.8443 |  | 1016.7475 |  | 140.5611
01/22 09:00:00 | 20.6765 | 21.1259 | 21.1345 | 20.7839 | 20.5674 | 21.0553 | 22.7742 | 19.0433 | 14.4112 | 13.127 | 18.0177 | 62.7209 | 20.5419 | 18.0667 | [14 empty] | 4.4005 |  | 0.95372 |  |  |  | 13.3627 |  | 24.401 |  | 0.0023991 |  | 1993.993 |  | 6.1265
01/22 10:00:00 | 20.6957 | 21.1003 | 21.1005 | 20.7724 | 21.9094 | 21.0764 | 23.0305 | 36.4007 | 36.6332 | 34.0969 | 41.4555 | 43.4371 | 46.6897 | 12.0073 | [14 empty] | 5.4514 |  | 595.0373 |  |  |  | 606.4303 |  | 487.9488 |  | 867.1957 |  | 987.8311 |  | 1202.8686
01/22 11:00:00 | 20.9345 | 21.3179 | 21.3184 | 21.0309 | 23.5763 | 21.4518 | 23.3345 | 48.4052 | 50.8677 | 48.417 | 56.7519 | 36.6305 | 56.7881 | 6.4994 | [14 empty] | 5.7596 |  | 1756.0967 |  |  |  | 1968.5487 |  | 1757.0869 |  | 2525.3174 |  | 907.8851 |  | 2528.9593
01/22 12:00:00 | 21.5862 | 22.4194 | 22.0363 | 22.2185 | 24.2209 | 22.8918 | 23.5967 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7978 | [14 empty] | 4.042 |  | 7.8279 |  |  |  | 7.8279 |  | 7.8279 |  | 7.8279 |  | 7.8279 |  | 7.8279
01/22 13:00:00 | 21.5806 | 23.2114 | 22.3132 | 22.7927 | 24.0917 | 23.6734 | 23.647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.2698 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/22 14:00:00 | 21.3885 | 23.2988 | 22.3009 | 22.7184 | 23.797 | 23.512 | 23.7357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 5.5093 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/22 15:00:00 | 21.2996 | 23.2534 | 22.2595 | 22.6303 | 23.5658 | 23.3933 | 23.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 6.6996 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/22 16:00:00 | 21.2664 | 23.2417 | 22.2681 | 22.6137 | 23.4312 | 23.3559 | 24.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 7.8316 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/22 17:00:00 | 21.2571 | 23.2494 | 22.3076 | 22.618 | 23.3589 | 23.3461 | 24.0631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 7.8738 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/22 18:00:00 | 21.2929 | 23.3025 | 22.3982 | 22.6729 | 23.3477 | 23.4009 | 23.8837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 6.712 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/22 19:00:00 | 21.2567 | 23.2752 | 22.4149 | 22.6288 | 23.2202 | 23.3455 | 23.6498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 5.7267 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/22 20:00:00 | 21.1881 | 23.1705 | 22.3747 | 22.5271 | 23.0224 | 23.2088 | 23.463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 5.1753 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/22 21:00:00 | 21.1206 | 23.0513 | 22.3228 | 22.4088 | 22.804 | 23.0342 | 23.3147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.814 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/22 22:00:00 | 21.0646 | 22.9277 | 22.2763 | 22.2765 | 22.625 | 22.883 | 23.1216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.2313 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/22 23:00:00 | 20.9934 | 22.7819 | 22.214 | 22.1238 | 22.4151 | 22.6991 | 22.8978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.6267 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/22 24:00:00 | 20.869 | 22.5779 | 22.1006 | 21.9424 | 22.188 | 22.4957 | 22.5908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.9646 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
01/23 01:00:00 | 20.6856 | 22.3573 | 21.9683 | 21.7344 | 21.9561 | 22.2847 | 22.4569 | 0 | 0 | 0 | 0 | 0 | 0 | 18.8576 | [14 empty] | 3.1377 |  | 355.6107 |  |  |  | 355.6107 |  | 355.6107 |  | 355.6107 |  | 355.6107 |  | 355.6107
01/23 02:00:00 | 20.513 | 22.1382 | 21.8416 | 21.5305 | 21.6945 | 22.047 | 22.4877 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6491 | [14 empty] | 3.8996 |  | 186.2989 |  |  |  | 186.2989 |  | 186.2989 |  | 186.2989 |  | 186.2989 |  | 186.2989
01/23 03:00:00 | 20.3456 | 21.9318 | 21.6692 | 21.3286 | 21.4479 | 21.8224 | 22.5669 | 0 | 0 | 0 | 0 | 0 | 0 | 11.3251 | [14 empty] | 4.9342 |  | 128.257 |  |  |  | 128.257 |  | 128.257 |  | 128.257 |  | 128.257 |  | 128.257
01/23 04:00:00 | 20.1848 | 21.7515 | 21.5057 | 21.1301 | 21.2307 | 21.6237 | 22.592 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2549 | [14 empty] | 5.7948 |  | 150.1825 |  |  |  | 150.1825 |  | 150.1825 |  | 150.1825 |  | 150.1825 |  | 150.1825
01/23 05:00:00 | 20.0768 | 21.6225 | 21.3956 | 20.9906 | 21.0359 | 21.4832 | 22.5822 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6462 | [14 empty] | 6.2773 |  | 159.9268 |  |  |  | 159.9268 |  | 159.9268 |  | 159.9268 |  | 159.9268 |  | 159.9268
01/23 06:00:00 | 20.0054 | 21.5 | 21.3241 | 20.8953 | 20.8561 | 21.3533 | 22.5601 | 0 | 0 | 0 | 0 | 0 | 0 | 12.8947 | [14 empty] | 6.5263 |  | 166.2739 |  |  |  | 166.2739 |  | 166.2739 |  | 166.2739 |  | 166.2739 |  | 166.2739
01/23 07:00:00 | 19.9288 | 21.3318 | 21.2474 | 20.7576 | 20.678 | 21.1753 | 22.5399 | 0 | 0 | 0 | 0 | 0 | 0 | 12.9304 | [14 empty] | 6.818 |  | 167.1951 |  |  |  | 167.1951 |  | 167.1951 |  | 167.1951 |  | 167.1951 |  | 167.1951
01/23 08:00:00 | 19.8496 | 21.2042 | 21.1674 | 20.6163 | 20.5403 | 21.0408 | 22.4966 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9947 | [14 empty] | 7.0065 |  | 440.7784 |  |  |  | 440.7784 |  | 440.7784 |  | 440.7784 |  | 440.7784 |  | 440.7784
01/23 09:00:00 | 19.7864 | 21.1287 | 21.1041 | 20.5318 | 20.4543 | 20.9593 | 22.5259 | 57.3686 | 66.0246 | 60.0744 | 70.3964 | 69.457 | 71.4372 | 23.4668 | [14 empty] | 7.5046 |  | 1149.3348 |  |  |  | 1811.1687 |  | 1340.1169 |  | 2202.3898 |  | 2115.1007 |  | 2301.1647
01/23 10:00:00 | 21.1874 | 22.5489 | 22.6066 | 22.1088 | 21.7224 | 22.6872 | 22.5893 | 50.4562 | 38.2351 | 40.7223 | 43.6683 | 42.9175 | 42.9394 | 21.8155 | [14 empty] | 1.9655 |  | 820.2911 |  |  |  | 269.6027 |  | 357.4688 |  | 477.545 |  | 445.2959 |  | 446.2197
01/23 11:00:00 | 23.1375 | 24.6659 | 24.5667 | 24.2751 | 23.9013 | 24.7821 | 22.6434 | 45.138 | 32.9149 | 36.3779 | 38.5789 | 35.7506 | 37.5395 | 15.0549 | [14 empty] | 0.24404 |  | 904.9909 |  |  |  | 318.9811 |  | 454.6689 |  | 553.3794 |  | 428.3135 |  | 505.5589
01/23 12:00:00 | 24.182 | 25.7071 | 25.394 | 25.3074 | 24.9961 | 25.681 | 22.6498 | 41.4814 | 31.268 | 34.3377 | 36.9231 | 34.4246 | 36.1184 | 18.9828 | [14 empty] | 2.3479 |  | 506.1866 |  |  |  | 150.9261 |  | 235.773 |  | 321.8554 |  | 238.4485 |  | 293.6284
01/23 13:00:00 | 24.5513 | 26.0935 | 25.6932 | 25.5807 | 25.2897 | 25.9457 | 22.6236 | 38.6694 | 29.6256 | 32.3154 | 34.5206 | 31.8426 | 33.8183 | 47.5022 | [14 empty] | 3.7159 |  | 78.0192 |  |  |  | 319.575 |  | 230.6393 |  | 168.5234 |  | 245.2224 |  | 187.2504
01/23 14:00:00 | 24.5427 | 26.1258 | 25.6381 | 25.4993 | 25.2257 | 25.9141 | 22.8884 | 30.8054 | 28.041 | 26.1859 | 32.7438 | 30.0266 | 32.1066 | 8.003 | [14 empty] | 2.7368 |  | 519.9512 |  |  |  | 401.5226 |  | 330.6177 |  | 612.1076 |  | 485.0397 |  | 580.9868
01/23 15:00:00 | 24.4738 | 26.1345 | 25.5666 | 25.4401 | 25.1557 | 25.8752 | 22.6972 | 35.55 | 26.6124 | 29.9028 | 30.8443 | 28.3272 | 30.5562 | 36.5143 | [14 empty] | 3.1563 |  | 0.92998 |  |  |  | 98.0472 |  | 43.7121 |  | 32.1494 |  | 67.0283 |  | 35.4985
01/23 16:00:00 | 24.6659 | 26.2835 | 25.7548 | 25.5428 | 25.2411 | 25.9878 | 22.8256 | 27.6329 | 25.2304 | 23.6226 | 28.6168 | 26.3513 | 28.6571 | 15.1922 | [14 empty] | 3.3868 |  | 154.7714 |  |  |  | 100.7673 |  | 71.0728 |  | 180.2206 |  | 124.5268 |  | 181.3043
01/23 17:00:00 | 24.7282 | 26.3924 | 25.8297 | 25.5964 | 25.281 | 26.0608 | 22.7691 | 31.2896 | 24.0501 | 26.6346 | 26.7053 | 24.6347 | 26.7401 | 40.3306 | [14 empty] | 3.8381 |  | 81.7403 |  |  |  | 265.054 |  | 187.581 |  | 185.6488 |  | 246.3631 |  | 184.7028
01/23 18:00:00 | 24.6475 | 26.3357 | 25.7359 | 25.4383 | 25.114 | 25.9531 | 22.7706 | 29.1575 | 23.2572 | 24.797 | 25.2512 | 23.3174 | 25.2061 | 48.5543 | [14 empty] | 3.5227 |  | 376.2366 |  |  |  | 639.9434 |  | 564.4102 |  | 543.0312 |  | 636.8995 |  | 545.1366
01/23 19:00:00 | 24.4429 | 26.1115 | 25.5079 | 25.0966 | 24.7606 | 25.6541 | 22.8497 | 28.4328 | 22.2878 | 24.0247 | 24.6096 | 22.7782 | 24.5192 | 28.8591 | [14 empty] | 2.5383 |  | 0.18173 |  |  |  | 43.1826 |  | 23.3718 |  | 18.0586 |  | 36.9779 |  | 18.8351
01/23 20:00:00 | 23.9681 | 25.609 | 25.0119 | 24.5013 | 24.1455 | 25.0587 | 22.8886 | 27.1178 | 21.4273 | 23.014 | 23.476 | 21.7937 | 23.3802 | 26.8927 | [14 empty] | 1.1652 |  | 0.050676 |  |  |  | 29.8698 |  | 15.0442 |  | 11.6738 |  | 25.9995 |  | 12.3376
01/23 21:00:00 | 23.3755 | 25.0367 | 24.3994 | 23.8596 | 23.4842 | 24.4199 | 22.6291 | 21.4943 | 15.7571 | 17.4872 | 18.3125 | 17.0163 | 18.2462 | 10.0124 | [14 empty] | 0.55718 |  | 131.835 |  |  |  | 33.0013 |  | 55.8731 |  | 68.8915 |  | 49.0544 |  | 67.7957
01/23 22:00:00 | 22.969 | 24.6088 | 23.9865 | 23.3056 | 22.9182 | 23.8657 | 22.1827 | 20.3892 | 15.318 | 16.7734 | 17.4795 | 16.2354 | 17.4121 | 17.3554 | [14 empty] | 0.61822 |  | 9.2038 |  |  |  | 4.1512 |  | 0.33873 |  | 0.015392 |  | 1.2544 |  | 0.0032089
01/23 23:00:00 | 22.6443 | 24.1985 | 23.6598 | 22.831 | 22.3918 | 23.3845 | 21.8623 | 19.7613 | 14.8326 | 16.2384 | 16.9285 | 15.7898 | 16.8688 | 19.9924 | [14 empty] | 0.61144 |  | 0.053417 |  |  |  | 26.6237 |  | 14.0926 |  | 9.3878 |  | 17.6619 |  | 9.7573
01/23 24:00:00 | 22.326 | 23.8306 | 23.3345 | 22.4164 | 21.9359 | 22.959 | 21.6963 | 18.2594 | 14.2465 | 15.3048 | 15.7265 | 14.6925 | 15.6664 | 20.493 | [14 empty] | 0.39653 |  | 4.9891 |  |  |  | 39.0189 |  | 26.9175 |  | 22.7191 |  | 33.6458 |  | 23.2961
01/24 01:00:00 | 22.0395 | 23.5296 | 23.0433 | 22.1146 | 21.6168 | 22.6494 | 21.6024 | 14.2971 | 13.6302 | 12.1169 | 14.8289 | 13.868 | 14.7754 | 21.8595 | [14 empty] | 0.19098 |  | 57.1902 |  |  |  | 67.7221 |  | 94.9197 |  | 49.4295 |  | 63.8652 |  | 50.1846
01/24 02:00:00 | 21.8458 | 23.2692 | 22.8518 | 21.8737 | 21.364 | 22.4022 | 21.5378 | 14.4197 | 13.2115 | 12.2162 | 14.5811 | 13.673 | 14.5547 | 22.0967 | [14 empty] | 0.094847 |  | 58.9369 |  |  |  | 78.9474 |  | 97.6242 |  | 56.4842 |  | 70.9594 |  | 56.8817
01/24 03:00:00 | 21.7021 | 23.0172 | 22.7095 | 21.6314 | 21.1116 | 22.1566 | 21.5543 | 13.5482 | 12.6935 | 11.6687 | 13.7486 | 12.8289 | 13.6899 | 21.6255 | [14 empty] | 0.021846 |  | 65.2423 |  |  |  | 79.78 |  | 99.1366 |  | 62.0455 |  | 77.3792 |  | 62.9727
01/24 04:00:00 | 21.5597 | 22.7721 | 22.5671 | 21.3926 | 20.8515 | 21.9131 | 21.4687 | 13.3008 | 12.2919 | 11.4039 | 13.3242 | 12.5055 | 13.2798 | 22.9753 | [14 empty] | 0.0082685 |  | 93.5959 |  |  |  | 114.1343 |  | 133.8969 |  | 93.1432 |  | 109.6171 |  | 94.0022
01/24 05:00:00 | 21.4128 | 22.5313 | 22.4198 | 21.1516 | 20.6041 | 21.6672 | 21.4913 | 12.6754 | 10.2697 | 10.9754 | 12.6985 | 11.8794 | 12.6533 | 22.0129 | [14 empty] | 0.0061666 |  | 87.1894 |  |  |  | 137.904 |  | 121.8256 |  | 86.7588 |  | 102.6879 |  | 87.6033
01/24 06:00:00 | 21.2641 | 22.3398 | 22.27 | 20.9123 | 20.3441 | 21.4247 | 21.4807 | 12.4616 | 10.2103 | 10.7401 | 11.0115 | 10.9453 | 11.0639 | 22.234 | [14 empty] | 0.046907 |  | 95.4982 |  |  |  | 144.5686 |  | 132.1079 |  | 125.9438 |  | 127.4333 |  | 124.7698
01/24 07:00:00 | 21.1133 | 22.1998 | 22.1187 | 20.7124 | 20.1447 | 21.2231 | 21.3498 | 11.6329 | 9.8539 | 10.2059 | 10.4305 | 22.588 | 10.4772 | 23.6571 | [14 empty] | 0.055941 |  | 144.5817 |  |  |  | 190.5307 |  | 180.9359 |  | 174.9432 |  | 1.1432 |  | 173.7119
01/24 08:00:00 | 20.9662 | 22.0484 | 21.9702 | 20.5708 | 20.1301 | 21.0798 | 21.566 | 15.1905 | 13.1673 | 13.4024 | 13.6607 | 63.0602 | 13.7425 | 75.7922 | [14 empty] | 0.35975 |  | 3672.5653 |  |  |  | 3921.8786 |  | 3892.4985 |  | 3860.3286 |  | 162.1058 |  | 3850.1756
01/24 09:00:00 | 20.8307 | 21.9119 | 21.8338 | 20.4378 | 20.974 | 20.9446 | 22.5566 | 38.3989 | 16.3558 | 17.4285 | 43.7889 | 57.9684 | 44.9225 | 47.8553 | [14 empty] | 2.9787 |  | 89.4233 |  |  |  | 992.2229 |  | 925.7902 |  | 16.536 |  | 102.2736 |  | 8.6013
01/24 10:00:00 | 21.0161 | 21.8485 | 21.8025 | 20.6659 | 22.6863 | 21.1758 | 22.9604 | 49.6623 | 29.6659 | 31.0979 | 57.7254 | 44.7186 | 58.3364 | 11.8227 | [14 empty] | 3.7806 |  | 1431.8372 |  |  |  | 318.3809 |  | 371.5334 |  | 2107.0528 |  | 1082.1407 |  | 2163.5206
01/24 11:00:00 | 21.9105 | 22.0661 | 22.1404 | 22.0885 | 24.23 | 22.7245 | 22.7257 | 42.6664 | 36.5569 | 35.3746 | 44.0645 | 39.5286 | 40.3224 | 24.0517 | [14 empty] | 0.6645 |  | 346.5042 |  |  |  | 156.3792 |  | 128.2082 |  | 400.51 |  | 239.5326 |  | 264.7343
01/24 12:00:00 | 22.903 | 22.8965 | 22.8239 | 23.9985 | 24.8664 | 24.5907 | 22.7824 | 36.5988 | 27.4335 | 29.185 | 36.9921 | 37.196 | 34.167 | 21.8604 | [14 empty] | 0.014551 |  | 217.2209 |  |  |  | 31.0599 |  | 53.6502 |  | 228.9702 |  | 235.1828 |  | 151.4522
01/24 13:00:00 | 23.3675 | 23.9794 | 23.3603 | 24.8059 | 25.0909 | 25.246 | 22.8429 | 34.21 | 23.6187 | 25.6422 | 34.3723 | 34.8845 | 32.4536 | 20.6826 | [14 empty] | 0.27518 |  | 182.9928 |  |  |  | 8.6209 |  | 24.5977 |  | 187.4082 |  | 201.6957 |  | 138.5577
01/24 14:00:00 | 23.441 | 24.2545 | 23.4546 | 24.7662 | 25.079 | 25.1837 | 22.7729 | 32.579 | 22.5437 | 24.6224 | 32.7306 | 33.0437 | 30.9376 | 22.0261 | [14 empty] | 0.44647 |  | 111.3642 |  |  |  | 0.26791 |  | 6.7411 |  | 114.5873 |  | 121.3884 |  | 79.4146
01/24 15:00:00 | 23.4987 | 24.3069 | 23.5408 | 24.7037 | 25.0765 | 25.1266 | 22.6838 | 30.53 | 21.3046 | 23.2502 | 30.4886 | 30.7146 | 28.8681 | 22.3178 | [14 empty] | 0.66407 |  | 67.4408 |  |  |  | 1.0266 |  | 0.86935 |  | 66.7624 |  | 70.5059 |  | 42.9063
01/24 16:00:00 | 23.6902 | 24.531 | 23.8171 | 24.8103 | 25.2095 | 25.2377 | 22.8048 | 24.9173 | 20.2027 | 19.0918 | 28.8477 | 29.0552 | 27.3406 | 21.0536 | [14 empty] | 0.78395 |  | 14.9286 |  |  |  | 0.72403 |  | 3.8485 |  | 60.7481 |  | 64.026 |  | 39.5268
01/24 17:00:00 | 23.7687 | 24.6837 | 23.9617 | 24.8768 | 25.2916 | 25.3062 | 22.8423 | 27.8624 | 19.1721 | 21.427 | 26.8425 | 27.0159 | 25.4948 | 21.3231 | [14 empty] | 0.85814 |  | 42.7615 |  |  |  | 4.6272 |  | 0.010786 |  | 30.4634 |  | 32.407 |  | 17.403
01/24 18:00:00 | 23.7222 | 24.6397 | 23.9041 | 24.769 | 25.1718 | 25.2027 | 22.6296 | 26.3338 | 18.2865 | 20.1153 | 25.63 | 25.7627 | 24.323 | 31.8773 | [14 empty] | 1.1938 |  | 30.7304 |  |  |  | 184.7086 |  | 138.3457 |  | 39.0293 |  | 37.3879 |  | 57.0677
01/24 19:00:00 | 23.5815 | 24.4794 | 23.7557 | 24.5505 | 24.9097 | 24.9477 | 22.7238 | 24.6101 | 17.4122 | 18.9686 | 23.7803 | 23.9552 | 22.614 | 28.0595 | [14 empty] | 0.73563 |  | 11.8978 |  |  |  | 113.3645 |  | 82.6436 |  | 18.311 |  | 16.845 |  | 29.6532
01/24 20:00:00 | 23.2216 | 24.1577 | 23.3822 | 24.1163 | 24.4349 | 24.4587 | 22.6766 | 23.0568 | 16.6201 | 17.915 | 22.285 | 22.4572 | 21.2289 | 33.5472 | [14 empty] | 0.29703 |  | 110.0474 |  |  |  | 286.5253 |  | 244.3657 |  | 126.8373 |  | 122.9883 |  | 151.7405
01/24 21:00:00 | 22.8513 | 23.7944 | 23.0025 | 23.6808 | 23.9279 | 24.0453 | 22.6139 | 17.8431 | 12.0685 | 13.427 | 16.8761 | 16.9883 | 16.1052 | 4.4696 | [14 empty] | 0.056398 |  | 178.8514 |  |  |  | 57.7434 |  | 80.234 |  | 153.9218 |  | 156.7174 |  | 135.3881
01/24 22:00:00 | 22.551 | 23.4495 | 22.6983 | 23.3258 | 23.4773 | 23.6974 | 22.259 | 14.299 | 11.7131 | 10.855 | 16.2278 | 16.334 | 15.4854 | 18.8703 | [14 empty] | 0.085252 |  | 20.8974 |  |  |  | 51.2259 |  | 64.246 |  | 6.9828 |  | 6.4332 |  | 11.4581
01/24 23:00:00 | 22.3133 | 23.123 | 22.4662 | 22.9441 | 23.0282 | 23.3216 | 22.0031 | 17.6321 | 11.4447 | 13.2545 | 16.4182 | 16.5551 | 15.7055 | 18.7332 | [14 empty] | 0.096248 |  | 1.2125 |  |  |  | 53.1222 |  | 30.0166 |  | 5.3593 |  | 4.7441 |  | 9.1671
01/24 24:00:00 | 22.1107 | 22.7971 | 22.2618 | 22.5126 | 22.6137 | 22.8907 | 21.8712 | 16.5192 | 11.1912 | 12.5022 | 15.6473 | 15.8112 | 14.988 | 18.5142 | [14 empty] | 0.057333 |  | 3.98 |  |  |  | 53.6255 |  | 36.144 |  | 8.219 |  | 7.3057 |  | 12.4335
01/25 01:00:00 | 21.8464 | 22.4954 | 21.9967 | 22.2066 | 22.2471 | 22.5829 | 21.7643 | 13.3492 | 9.3918 | 10.1881 | 14.9242 | 15.1138 | 14.331 | 19.45 | [14 empty] | 0.0067508 |  | 37.2198 |  |  |  | 101.1689 |  | 85.7836 |  | 20.483 |  | 18.8033 |  | 26.2041
01/25 02:00:00 | 21.6671 | 22.2962 | 21.8247 | 21.9773 | 22.0069 | 22.3533 | 21.6835 | 13.0012 | 9.2982 | 10.0212 | 14.3469 | 14.5355 | 13.7549 | 19.8521 | [14 empty] | 0.00027096 |  | 46.9356 |  |  |  | 111.3849 |  | 96.647 |  | 30.3073 |  | 28.2663 |  | 37.1759
01/25 03:00:00 | 21.5327 | 22.1521 | 21.6865 | 21.754 | 21.786 | 22.1273 | 21.6906 | 13.0314 | 9.1508 | 9.9806 | 14.1843 | 14.339 | 13.5852 | 20.1542 | [14 empty] | 0.024942 |  | 50.7344 |  |  |  | 121.0736 |  | 103.502 |  | 35.6393 |  | 33.8167 |  | 43.1512
01/25 04:00:00 | 21.3967 | 22.008 | 21.5549 | 21.5277 | 21.5553 | 21.886 | 21.6222 | 12.2895 | 8.9041 | 9.5847 | 12.0335 | 13.5726 | 12.8436 | 20.7088 | [14 empty] | 0.050853 |  | 70.8858 |  |  |  | 139.3516 |  | 123.7458 |  | 75.2622 |  | 50.9256 |  | 61.8617
01/25 05:00:00 | 21.2555 | 21.861 | 21.4188 | 21.3426 | 21.3183 | 21.6485 | 21.5472 | 11.716 | 8.6326 | 9.2301 | 11.5885 | 12.8661 | 12.215 | 21.6351 | [14 empty] | 0.085089 |  | 98.3875 |  |  |  | 169.0652 |  | 153.8829 |  | 100.9329 |  | 76.8948 |  | 88.7366
01/25 06:00:00 | 21.1122 | 21.7119 | 21.2801 | 21.2001 | 21.068 | 21.4121 | 21.4904 | 11.5111 | 8.4261 | 9.0505 | 11.361 | 12.5213 | 10.839 | 21.9641 | [14 empty] | 0.14309 |  | 109.2667 |  |  |  | 183.2792 |  | 166.7628 |  | 112.4266 |  | 89.1669 |  | 123.7694
01/25 07:00:00 | 20.9631 | 21.5587 | 21.1371 | 21.0404 | 20.8102 | 21.2215 | 21.4499 | 10.5307 | 8.1293 | 8.5143 | 10.4314 | 11.5501 | 10.0273 | 21.2584 | [14 empty] | 0.23702 |  | 115.0854 |  |  |  | 172.3757 |  | 162.4143 |  | 117.2241 |  | 94.2525 |  | 126.1385
01/25 08:00:00 | 20.8132 | 21.405 | 20.9928 | 20.8797 | 20.5527 | 21.0766 | 21.7671 | 12.4149 | 10.4674 | 10.4192 | 37.3723 | 40.3897 | 38.3342 | 75.9858 | [14 empty] | 0.90987 |  | 4041.2615 |  |  |  | 4292.6618 |  | 4298.9864 |  | 1491.0069 |  | 1267.0866 |  | 1417.6416
01/25 09:00:00 | 20.674 | 21.2639 | 20.862 | 20.8503 | 20.5182 | 21.0802 | 22.8173 | 36.087 | 38.9342 | 36.0502 | 57.2512 | 59.9922 | 58.3077 | 29.5076 | [14 empty] | 4.594 |  | 43.2885 |  |  |  | 88.8624 |  | 42.8064 |  | 769.7117 |  | 929.3122 |  | 829.4509
01/25 10:00:00 | 20.8454 | 21.4183 | 21.063 | 21.8423 | 21.8164 | 22.2229 | 23.0549 | 48.0139 | 51.4666 | 48.9937 | 42.9423 | 43.171 | 42.4174 | 15.3123 | [14 empty] | 4.8819 |  | 1069.3926 |  |  |  | 1307.1322 |  | 1134.4359 |  | 763.4171 |  | 776.1068 |  | 734.6832
01/25 11:00:00 | 21.7469 | 22.6877 | 22.0991 | 23.6452 | 23.8744 | 24.1262 | 23.0783 | 41.0956 | 35.6984 | 39.7253 | 36.9408 | 36.4873 | 36.1357 | 16.7156 | [14 empty] | 1.7725 |  | 594.3825 |  |  |  | 360.3456 |  | 529.4469 |  | 409.0588 |  | 390.9201 |  | 377.1384
01/25 12:00:00 | 22.8906 | 24.7081 | 23.6951 | 24.6045 | 24.6846 | 24.9667 | 23.3861 | 34.9885 | 29.7289 | 33.4467 | 33.5773 | 33.2809 | 32.8742 | 7.352 | [14 empty] | 0.2456 |  | 763.7752 |  |  |  | 500.7232 |  | 680.931 |  | 687.7642 |  | 672.3039 |  | 651.3811
01/25 13:00:00 | 23.5991 | 25.6998 | 24.6416 | 24.9415 | 25.0036 | 25.3432 | 23.605 | 30.2911 | 26.4621 | 29.2271 | 28.8814 | 28.7564 | 27.9653 | 2.9654 | [14 empty] | 3.4534e-05 |  | 746.6921 |  |  |  | 552.0925 |  | 689.6733 |  | 671.6397 |  | 665.1755 |  | 624.9945
01/25 14:00:00 | 23.9606 | 25.9932 | 25.0409 | 25.1054 | 25.2112 | 25.629 | 23.657 | 28.5852 | 23.2221 | 26.8035 | 26.9228 | 26.3864 | 25.4471 | 2.7347 | [14 empty] | 0.092164 |  | 668.2484 |  |  |  | 419.7361 |  | 579.3098 |  | 585.0649 |  | 559.4047 |  | 515.8573
01/25 15:00:00 | 24.363 | 26.3994 | 25.4923 | 25.4397 | 25.5789 | 26.0342 | 23.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6181 | [14 empty] | 0.48476 |  | 6.8546 |  |  |  | 6.8546 |  | 6.8546 |  | 6.8546 |  | 6.8546 |  | 6.8546
01/25 16:00:00 | 24.4265 | 26.6372 | 25.6508 | 25.5814 | 25.7451 | 26.2122 | 23.3686 | 0 | 0 | 0 | 0 | 0 | 0 | 13.7169 | [14 empty] | 1.1192 |  | 188.1544 |  |  |  | 188.1544 |  | 188.1544 |  | 188.1544 |  | 188.1544 |  | 188.1544
01/25 17:00:00 | 24.2793 | 26.6152 | 25.5848 | 25.507 | 25.6684 | 26.1496 | 23.2389 | 0 | 0 | 0 | 0 | 0 | 0 | 13.4913 | [14 empty] | 1.0823 |  | 182.0156 |  |  |  | 182.0156 |  | 182.0156 |  | 182.0156 |  | 182.0156 |  | 182.0156
01/25 18:00:00 | 23.9623 | 26.2987 | 25.3186 | 25.1804 | 25.3232 | 25.7953 | 23.0293 | 0 | 0 | 0 | 0 | 0 | 0 | 15.2824 | [14 empty] | 0.87063 |  | 233.5512 |  |  |  | 233.5512 |  | 233.5512 |  | 233.5512 |  | 233.5512 |  | 233.5512
01/25 19:00:00 | 23.5492 | 25.7799 | 24.9453 | 24.7017 | 24.8406 | 25.272 | 22.8276 | 0 | 0 | 0 | 0 | 0 | 0 | 17.4617 | [14 empty] | 0.52061 |  | 304.9103 |  |  |  | 304.9103 |  | 304.9103 |  | 304.9103 |  | 304.9103 |  | 304.9103
01/25 20:00:00 | 22.9525 | 25.1713 | 24.3781 | 24.0122 | 24.1372 | 24.6793 | 22.8578 | 0 | 0 | 0 | 0 | 0 | 0 | 15.256 | [14 empty] | 0.0089717 |  | 232.7448 |  |  |  | 232.7448 |  | 232.7448 |  | 232.7448 |  | 232.7448 |  | 232.7448
01/25 21:00:00 | 22.4961 | 24.6208 | 23.9438 | 23.5316 | 23.5822 | 24.1489 | 22.8265 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6065 | [14 empty] | 0.10917 |  | 74.0723 |  |  |  | 74.0723 |  | 74.0723 |  | 74.0723 |  | 74.0723 |  | 74.0723
01/25 22:00:00 | 22.1547 | 24.2292 | 23.6223 | 23.2064 | 23.1327 | 23.7853 | 22.6422 | 0 | 0 | 0 | 0 | 0 | 0 | 12.0752 | [14 empty] | 0.23767 |  | 145.8114 |  |  |  | 145.8114 |  | 145.8114 |  | 145.8114 |  | 145.8114 |  | 145.8114
01/25 23:00:00 | 21.837 | 23.8324 | 23.3238 | 22.8399 | 22.6876 | 23.3557 | 22.5195 | 0 | 0 | 0 | 0 | 0 | 0 | 13.899 | [14 empty] | 0.46578 |  | 193.1828 |  |  |  | 193.1828 |  | 193.1828 |  | 193.1828 |  | 193.1828 |  | 193.1828
01/25 24:00:00 | 21.518 | 23.477 | 23.0614 | 22.4429 | 22.3063 | 22.9535 | 22.4456 | 0 | 0 | 0 | 0 | 0 | 0 | 12.8874 | [14 empty] | 0.86033 |  | 166.0855 |  |  |  | 166.0855 |  | 166.0855 |  | 166.0855 |  | 166.0855 |  | 166.0855
01/26 01:00:00 | 21.251 | 23.2007 | 22.8876 | 22.1817 | 22.0577 | 22.6991 | 22.4057 | 0 | 0 | 0 | 0 | 0 | 0 | 14.3852 | [14 empty] | 1.3332 |  | 206.9348 |  |  |  | 206.9348 |  | 206.9348 |  | 206.9348 |  | 206.9348 |  | 206.9348
01/26 02:00:00 | 21.1086 | 22.9712 | 22.7967 | 21.9932 | 21.8724 | 22.5143 | 22.2783 | 0 | 0 | 0 | 0 | 0 | 0 | 15.063 | [14 empty] | 1.3682 |  | 226.894 |  |  |  | 226.894 |  | 226.894 |  | 226.894 |  | 226.894 |  | 226.894
01/26 03:00:00 | 21.0091 | 22.7995 | 22.6929 | 21.8496 | 21.685 | 22.3706 | 22.2155 | 30.6832 | 33.042 | 30.5835 | 32.7845 | 34.9248 | 33.5814 | 15.1085 | [14 empty] | 1.4554 |  | 242.5696 |  |  |  | 321.6104 |  | 239.475 |  | 312.4417 |  | 392.6858 |  | 341.249
01/26 04:00:00 | 21.3607 | 23.0113 | 23.0108 | 22.1104 | 21.9104 | 22.624 | 22.1286 | 23.5498 | 20.3273 | 21.33 | 21.6696 | 21.7407 | 21.5331 | 16.7383 | [14 empty] | 0.5896 |  | 46.397 |  |  |  | 12.8806 |  | 21.0834 |  | 24.318 |  | 25.0237 |  | 22.9903
01/26 05:00:00 | 21.6515 | 23.1824 | 23.2593 | 22.2999 | 22.1011 | 22.8037 | 21.9769 | 18.1792 | 18.5673 | 19.9348 | 20.1879 | 20.055 | 19.962 | 18.0654 | [14 empty] | 0.10588 |  | 0.012957 |  |  |  | 0.25187 |  | 3.4946 |  | 4.5051 |  | 3.9584 |  | 3.597
01/26 06:00:00 | 21.7307 | 23.2511 | 23.3652 | 22.3532 | 22.1488 | 22.8468 | 21.8122 | 22.0419 | 17.8081 | 19.1762 | 19.5112 | 19.3817 | 19.2948 | 19.1462 | [14 empty] | 0.0066318 |  | 8.3849 |  |  |  | 1.7905 |  | 0.00089976 |  | 0.13323 |  | 0.055463 |  | 0.022097
01/26 07:00:00 | 21.747 | 23.2378 | 23.3585 | 22.3023 | 22.0886 | 22.7875 | 21.6525 | 21.0576 | 17.2648 | 18.6334 | 19.0877 | 18.9699 | 18.8851 | 19.7129 | [14 empty] | 0.0089249 |  | 1.8081 |  |  |  | 5.9935 |  | 1.1653 |  | 0.39095 |  | 0.552 |  | 0.68525
01/26 08:00:00 | 21.7124 | 23.1619 | 23.278 | 22.1797 | 21.954 | 22.657 | 21.8567 | 20.3926 | 22.5146 | 22.509 | 20.6232 | 24.0199 | 23.2384 | 76.5007 | [14 empty] | 0.020819 |  | 3148.1109 |  |  |  | 2914.4949 |  | 2915.1033 |  | 3122.2941 |  | 2754.2349 |  | 2836.8717
01/26 09:00:00 | 21.6276 | 23.0889 | 23.1728 | 22.0575 | 21.826 | 22.5323 | 22.755 | 38.6111 | 21.0461 | 21.9329 | 23.5539 | 34.1236 | 26.2209 | 26.6258 | [14 empty] | 1.2709 |  | 143.6467 |  |  |  | 31.1332 |  | 22.023 |  | 9.4365 |  | 56.2161 |  | 0.16399
01/26 10:00:00 | 21.7754 | 23.096 | 23.154 | 22.0369 | 21.8845 | 22.5122 | 22.7722 | 42.5395 | 19.9734 | 21.072 | 33.2237 | 43.1892 | 37.6783 | 21.286 | [14 empty] | 0.9937 |  | 451.7124 |  |  |  | 1.7228 |  | 0.045762 |  | 142.5104 |  | 479.7499 |  | 268.7087
01/26 11:00:00 | 22.3991 | 23.2417 | 23.286 | 22.2172 | 22.5214 | 22.8187 | 22.6676 | 39.4977 | 18.8612 | 19.9451 | 42.2575 | 42.6256 | 32.2144 | 24.3275 | [14 empty] | 0.0721 |  | 230.1336 |  |  |  | 29.8805 |  | 19.2055 |  | 321.4852 |  | 334.8206 |  | 62.2031
01/26 12:00:00 | 23.0378 | 23.4233 | 23.4543 | 22.8406 | 23.4205 | 23.455 | 22.7175 | 35.7578 | 15.7953 | 16.1483 | 33.4455 | 35.3728 | 26.6739 | 24.3749 | [14 empty] | 0.10259 |  | 129.5702 |  |  |  | 73.6089 |  | 67.6762 |  | 82.2753 |  | 120.9547 |  | 5.2855
01/26 13:00:00 | 23.3952 | 23.5309 | 23.5439 | 23.6365 | 24.0271 | 23.8534 | 22.6105 | 32.8923 | 17.1692 | 17.8602 | 29.0462 | 31.0338 | 25.1165 | 26.4795 | [14 empty] | 0.61581 |  | 41.1231 |  |  |  | 86.6824 |  | 74.2934 |  | 6.5876 |  | 20.7409 |  | 1.8579
01/26 14:00:00 | 23.3787 | 23.3839 | 23.354 | 23.7799 | 24.0899 | 23.7755 | 22.5225 | 26.7685 | 14.3083 | 14.6531 | 27.7014 | 26.9987 | 23.8774 | 25.9593 | [14 empty] | 0.73304 |  | 0.65491 |  |  |  | 135.7454 |  | 127.8295 |  | 3.0349 |  | 1.0804 |  | 4.3342
01/26 15:00:00 | 23.3164 | 23.2968 | 23.2318 | 23.7118 | 24.0648 | 23.6978 | 22.6918 | 30.1529 | 15.3741 | 16.1392 | 26.0046 | 28.3473 | 22.4259 | 44.2255 | [14 empty] | 0.39018 |  | 198.0355 |  |  |  | 832.4017 |  | 788.8358 |  | 331.9997 |  | 252.1157 |  | 475.2225
01/26 16:00:00 | 23.5154 | 23.4632 | 23.3958 | 23.836 | 24.2382 | 23.8443 | 22.8916 | 23.9938 | 12.6796 | 13.133 | 24.3484 | 26.1036 | 21.0196 | 21.5491 | [14 empty] | 0.38908 |  | 5.9769 |  |  |  | 78.6674 |  | 70.8296 |  | 7.8362 |  | 20.7435 |  | 0.28035
01/26 17:00:00 | 23.5976 | 23.5487 | 23.4635 | 23.8925 | 24.3226 | 23.9175 | 22.7704 | 26.1115 | 13.6449 | 14.1406 | 22.2531 | 23.8395 | 19.1593 | 25.5296 | [14 empty] | 0.68428 |  | 0.33867 |  |  |  | 141.246 |  | 129.7082 |  | 10.7356 |  | 2.8565 |  | 40.581
01/26 18:00:00 | 23.5445 | 23.5 | 23.3859 | 23.7913 | 24.2414 | 23.8298 | 22.6268 | 25.1557 | 12.9615 | 13.746 | 21.7678 | 23.2061 | 18.8965 | 26.5477 | [14 empty] | 0.84207 |  | 1.9375 |  |  |  | 184.5847 |  | 163.8827 |  | 22.847 |  | 11.1659 |  | 58.5399
01/26 19:00:00 | 23.358 | 23.2737 | 23.1246 | 23.5047 | 23.9608 | 23.5444 | 22.5153 | 24.2286 | 12.6741 | 13.422 | 20.9164 | 22.2707 | 18.3078 | 46.2759 | [14 empty] | 0.71022 |  | 486.0814 |  |  |  | 1129.0822 |  | 1079.3761 |  | 643.1022 |  | 576.2498 |  | 782.2166
01/26 20:00:00 | 22.9415 | 22.8008 | 22.6116 | 22.972 | 23.4272 | 23.0081 | 22.774 | 23.2692 | 12.2944 | 13.5792 | 20.0773 | 21.3393 | 17.6159 | 24.4747 | [14 empty] | 0.028052 |  | 1.4534 |  |  |  | 148.3596 |  | 118.7122 |  | 19.3379 |  | 9.8311 |  | 47.0436
01/26 21:00:00 | 22.4285 | 22.3715 | 22.18 | 22.5161 | 22.8662 | 22.5494 | 22.5145 | 18.4003 | 9.2137 | 10.9547 | 15.6902 | 16.6065 | 13.8894 | 11.6831 | [14 empty] | 0.0073848 |  | 45.1202 |  |  |  | 6.098 |  | 0.5306 |  | 16.0569 |  | 24.2398 |  | 4.8677
01/26 22:00:00 | 22.0621 | 22.0126 | 21.8593 | 22.1319 | 22.3596 | 22.1612 | 21.9449 | 17.2525 | 8.9461 | 9.91 | 14.7502 | 15.6473 | 13.0622 | 20.7073 | [14 empty] | 0.013725 |  | 11.9363 |  |  |  | 138.3276 |  | 116.5826 |  | 35.4874 |  | 25.6037 |  | 58.4479
01/26 23:00:00 | 21.7484 | 21.667 | 21.5295 | 21.7636 | 21.8853 | 21.7882 | 21.6315 | 16.6014 | 8.691 | 9.8317 | 14.2097 | 15.0775 | 12.5981 | 22.3794 | [14 empty] | 0.013666 |  | 33.3843 |  |  |  | 187.3709 |  | 157.4438 |  | 66.7428 |  | 53.3178 |  | 95.6722
01/26 24:00:00 | 21.4011 | 21.2661 | 21.1597 | 21.3475 | 21.4284 | 21.3639 | 21.4022 | 16.3987 | 8.6215 | 9.7764 | 14.1503 | 14.9918 | 12.6154 | 24.5003 | [14 empty] | 1.2522e-06 |  | 65.6366 |  |  |  | 252.138 |  | 216.7931 |  | 107.122 |  | 90.4115 |  | 141.251
01/27 01:00:00 | 21.0756 | 20.887 | 20.8176 | 20.9589 | 21.0747 | 20.9669 | 21.1736 | 15.3838 | 8.48 | 9.4164 | 13.3201 | 14.1181 | 11.8873 | 26.8939 | [14 empty] | 0.0096013 |  | 132.4838 |  |  |  | 339.073 |  | 305.4628 |  | 184.2489 |  | 163.2228 |  | 225.1983
01/27 02:00:00 | 20.8092 | 20.5856 | 20.5439 | 20.6407 | 20.7214 | 20.6465 | 21.0457 | 14.9602 | 8.2712 | 9.3909 | 12.9987 | 13.7559 | 11.6315 | 26.429 | [14 empty] | 0.055953 |  | 131.5318 |  |  |  | 329.7041 |  | 290.2962 |  | 180.373 |  | 160.6062 |  | 218.965
01/27 03:00:00 | 20.5413 | 20.2909 | 20.2797 | 20.3258 | 20.3774 | 20.3339 | 21.0213 | 12.0192 | 26.6943 | 26.0312 | 30.9621 | 32.74 | 31.1291 | 26.3374 | [14 empty] | 0.23041 |  | 205.011 |  |  |  | 0.1274 |  | 0.093738 |  | 21.3883 |  | 40.9937 |  | 22.9607
01/27 04:00:00 | 20.3214 | 20.1533 | 20.1901 | 20.18 | 20.2312 | 20.1962 | 20.9234 | 11.7224 | 39.2678 | 39.3144 | 43.9433 | 45.2686 | 44.5604 | 27.2814 | [14 empty] | 0.36243 |  | 242.0833 |  |  |  | 143.6724 |  | 144.7912 |  | 277.6165 |  | 323.5367 |  | 298.5616
01/27 05:00:00 | 20.1538 | 20.3892 | 20.5317 | 20.4342 | 20.4661 | 20.4666 | 20.8208 | 19.8857 | 38.4788 | 31.7549 | 43.6059 | 44.1666 | 43.7995 | 28.1393 | [14 empty] | 0.44496 |  | 68.1205 |  |  |  | 106.9068 |  | 13.0728 |  | 239.216 |  | 256.8768 |  | 245.2426
01/27 06:00:00 | 20.0804 | 20.7556 | 20.9242 | 20.8026 | 20.8087 | 20.8573 | 20.7348 | 40.973 | 32.446 | 27.4507 | 37.8432 | 37.7461 | 37.5096 | 29.108 | [14 empty] | 0.42823 |  | 140.779 |  |  |  | 11.1422 |  | 2.7467 |  | 76.3036 |  | 74.6166 |  | 70.5873
01/27 07:00:00 | 20.3245 | 21.1009 | 21.1057 | 21.1184 | 21.1013 | 21.1964 | 20.6817 | 42.0591 | 28.9586 | 21.5923 | 28.5715 | 33.3538 | 33.1342 | 29.4192 | [14 empty] | 0.1276 |  | 159.7687 |  |  |  | 0.21209 |  | 61.2595 |  | 0.71863 |  | 15.4809 |  | 13.8015
01/27 08:00:00 | 20.6986 | 21.315 | 21.1244 | 21.2013 | 21.2261 | 21.3646 | 21.0331 | 52.3359 | 50.0096 | 28.3489 | 56.8542 | 58.4163 | 56.9516 | 81.2284 | [14 empty] | 0.11186 |  | 834.773 |  |  |  | 974.6084 |  | 2796.2332 |  | 594.1001 |  | 520.3876 |  | 589.359
01/27 09:00:00 | 21.0907 | 21.9075 | 21.1073 | 21.6975 | 21.8941 | 22.0646 | 22.1218 | 52.1864 | 42.1098 | 45.3466 | 55.8989 | 48.7563 | 48.0632 | 65.1413 | [14 empty] | 1.0631 |  | 167.8285 |  |  |  | 530.4503 |  | 391.8311 |  | 85.4215 |  | 268.4682 |  | 291.6621
01/27 10:00:00 | 21.655 | 23.1167 | 21.4668 | 22.9133 | 22.857 | 23.1467 | 22.9189 | 51.4135 | 36.5755 | 50.7089 | 46.2143 | 41.2483 | 41.0516 | 24.7609 | [14 empty] | 1.5975 |  | 710.3627 |  |  |  | 139.5869 |  | 673.3 |  | 460.2516 |  | 271.8345 |  | 265.3891
01/27 11:00:00 | 22.4598 | 23.9389 | 22.6121 | 24.0715 | 23.4852 | 23.8363 | 22.7837 | 46.5777 | 34.0072 | 42.0237 | 41.6378 | 37.9545 | 37.7083 | 30.4196 | [14 empty] | 0.10489 |  | 261.0829 |  |  |  | 12.8706 |  | 134.6557 |  | 125.8471 |  | 56.7737 |  | 53.1247
01/27 12:00:00 | 23.192 | 24.3719 | 23.9778 | 24.535 | 23.8746 | 24.2117 | 22.7385 | 42.5367 | 31.7436 | 38.1119 | 39.2733 | 35.3888 | 35.1219 | 50.519 | [14 empty] | 0.20572 |  | 63.7176 |  |  |  | 352.5156 |  | 153.9365 |  | 126.4665 |  | 228.9228 |  | 237.0716
01/27 13:00:00 | 23.5342 | 24.6459 | 24.5418 | 24.7169 | 24.0983 | 24.4317 | 23.0423 | 40.1855 | 29.6402 | 35.6829 | 36.8146 | 32.9309 | 32.684 | 21.1015 | [14 empty] | 0.24197 |  | 364.2002 |  |  |  | 72.9094 |  | 212.6161 |  | 246.9021 |  | 139.9333 |  | 134.1534
01/27 14:00:00 | 23.5023 | 24.6223 | 24.4609 | 24.5923 | 23.9947 | 24.3333 | 22.8116 | 36.6688 | 27.1847 | 32.6308 | 33.2948 | 29.8118 | 29.4251 | 29.5242 | [14 empty] | 0.47709 |  | 51.0452 |  |  |  | 5.473 |  | 9.651 |  | 14.2175 |  | 0.082733 |  | 0.0098167
01/27 15:00:00 | 23.5744 | 24.7071 | 24.4564 | 24.5724 | 23.991 | 24.3655 | 22.6289 | 34.5061 | 25.421 | 30.5857 | 31.2354 | 28.011 | 27.7206 | 58.237 | [14 empty] | 0.89398 |  | 563.1555 |  |  |  | 1076.8923 |  | 764.5923 |  | 729.089 |  | 913.6126 |  | 931.2483
01/27 16:00:00 | 23.7823 | 24.9662 | 24.6414 | 24.7256 | 24.1852 | 24.5754 | 22.7657 | 28.6667 | 24.3443 | 29.5693 | 30.5429 | 27.5199 | 27.297 | 20.2292 | [14 empty] | 1.0335 |  | 71.1925 |  |  |  | 16.9344 |  | 87.2383 |  | 106.3743 |  | 53.1555 |  | 49.9542
01/27 17:00:00 | 23.8107 | 25.0982 | 24.7273 | 24.768 | 24.2471 | 24.642 | 22.7644 | 32.2267 | 23.1087 | 27.6853 | 28.177 | 25.4916 | 25.282 | 39.6412 | [14 empty] | 1.0947 |  | 54.9749 |  |  |  | 273.3245 |  | 142.9439 |  | 131.4287 |  | 200.2118 |  | 206.1872
01/27 18:00:00 | 23.726 | 24.9994 | 24.63 | 24.5897 | 24.0593 | 24.4872 | 22.7067 | 29.833 | 21.9825 | 26.1349 | 26.4412 | 23.9719 | 23.7648 | 56.757 | [14 empty] | 1.0391 |  | 724.899 |  |  |  | 1209.2651 |  | 937.7126 |  | 919.0452 |  | 1074.8624 |  | 1088.482
01/27 19:00:00 | 23.529 | 24.7379 | 24.4032 | 24.2484 | 23.7236 | 24.1709 | 22.8024 | 28.3632 | 20.9974 | 24.8557 | 25.0567 | 22.7408 | 22.5384 | 35.0565 | [14 empty] | 0.52792 |  | 44.7994 |  |  |  | 197.6566 |  | 104.0563 |  | 99.9954 |  | 151.6741 |  | 156.701
01/27 20:00:00 | 23.1074 | 24.2314 | 23.9552 | 23.7095 | 23.1856 | 23.6095 | 22.8788 | 26.7954 | 20.0345 | 23.5792 | 23.6561 | 21.4995 | 21.331 | 30.4937 | [14 empty] | 0.052241 |  | 13.6775 |  |  |  | 109.3956 |  | 47.8098 |  | 46.7531 |  | 80.8953 |  | 83.956
01/27 21:00:00 | 22.5768 | 23.7739 | 23.3984 | 23.1378 | 22.5981 | 23.0228 | 22.4915 | 20.793 | 14.6458 | 17.6064 | 18.0015 | 16.3714 | 16.2935 | 11.3192 | [14 empty] | 0.0072861 |  | 89.7513 |  |  |  | 11.0661 |  | 39.5288 |  | 44.652 |  | 25.5245 |  | 24.743
01/27 22:00:00 | 22.1948 | 23.3191 | 23.0114 | 22.6181 | 22.0688 | 22.4963 | 21.8097 | 19.3734 | 14.1344 | 16.6489 | 16.8395 | 15.3151 | 15.2507 | 22.4289 | [14 empty] | 0.14827 |  | 9.3364 |  |  |  | 68.7991 |  | 33.4085 |  | 31.2412 |  | 50.6068 |  | 51.5272
01/27 23:00:00 | 21.8784 | 22.8131 | 22.6937 | 22.1502 | 21.5488 | 22.0291 | 21.3937 | 19.4625 | 13.8682 | 16.5287 | 16.9717 | 15.5285 | 15.4164 | 25.4736 | [14 empty] | 0.23496 |  | 36.1337 |  |  |  | 134.6856 |  | 80.0112 |  | 72.282 |  | 98.9059 |  | 101.1482
01/27 24:00:00 | 21.54 | 22.3504 | 22.3507 | 21.7054 | 21.0625 | 21.5866 | 21.1219 | 18.7819 | 13.5889 | 16.0685 | 16.5306 | 15.1651 | 15.04 | 27.9417 | [14 empty] | 0.17479 |  | 83.9016 |  |  |  | 206.0028 |  | 140.9713 |  | 130.2127 |  | 163.2411 |  | 166.4538
01/28 01:00:00 | 21.2156 | 21.9947 | 22.0221 | 21.2749 | 20.6107 | 21.2406 | 20.9428 | 18.3252 | 13.2964 | 15.6871 | 16.2029 | 14.9123 | 14.7865 | 28.9598 | [14 empty] | 0.074437 |  | 113.0948 |  |  |  | 245.3431 |  | 176.1643 |  | 162.7394 |  | 197.3341 |  | 200.8836
01/28 02:00:00 | 20.9322 | 21.6823 | 21.736 | 20.9426 | 20.1866 | 20.9254 | 20.7655 | 18.2041 | 13.0219 | 15.495 | 16.1761 | 33.438 | 14.7905 | 29.2461 | [14 empty] | 0.027795 |  | 121.9264 |  |  |  | 263.2253 |  | 189.0943 |  | 170.8262 |  | 17.5722 |  | 208.9637
01/28 03:00:00 | 20.6478 | 21.3647 | 21.4484 | 20.6268 | 19.9977 | 20.6005 | 20.7174 | 17.7945 | 12.7892 | 15.1607 | 15.8618 | 45.6578 | 14.5506 | 30.3633 | [14 empty] | 0.0048573 |  | 157.9742 |  |  |  | 308.8485 |  | 231.121 |  | 210.2941 |  | 233.9219 |  | 250.042
01/28 04:00:00 | 20.3679 | 21.0494 | 21.1654 | 20.31 | 20.1977 | 20.2763 | 20.6557 | 14.6427 | 12.4666 | 12.4703 | 32.7161 | 45.4923 | 32.8352 | 29.8143 | [14 empty] | 0.082815 |  | 230.1782 |  |  |  | 300.9441 |  | 300.8152 |  | 8.4202 |  | 245.7983 |  | 9.126
01/28 05:00:00 | 20.1451 | 20.7528 | 20.9422 | 20.164 | 20.5157 | 20.1284 | 20.6155 | 23.0821 | 12.0876 | 12.3511 | 44.5967 | 39.0647 | 45.1885 | 30.9253 | [14 empty] | 0.22129 |  | 61.5167 |  |  |  | 354.86 |  | 345.0018 |  | 186.9052 |  | 66.2493 |  | 203.4385
01/28 06:00:00 | 20.0723 | 20.4518 | 20.7757 | 20.3813 | 20.7878 | 20.3587 | 20.5671 | 42.069 | 28.1495 | 11.9388 | 44.707 | 34.9715 | 44.9163 | 31.5357 | [14 empty] | 0.24485 |  | 110.9495 |  |  |  | 11.4664 |  | 384.0396 |  | 173.4833 |  | 11.8047 |  | 179.0388
01/28 07:00:00 | 20.2932 | 20.2915 | 20.6001 | 20.6956 | 20.8857 | 20.6942 | 20.5138 | 43.9318 | 39.2119 | 11.7232 | 39.2219 | 33.9428 | 38.9375 | 31.8766 | [14 empty] | 0.048665 |  | 145.327 |  |  |  | 53.8068 |  | 406.1625 |  | 53.953 |  | 4.2692 |  | 49.8551
01/28 08:00:00 | 20.6132 | 20.4551 | 20.4124 | 20.9551 | 20.874 | 20.9761 | 20.4798 | 40.212 | 38.9176 | 11.6238 | 36.0792 | 32.8747 | 35.6752 | 31.3702 | [14 empty] | 0.017801 |  | 78.1772 |  |  |  | 56.9633 |  | 389.9223 |  | 22.175 |  | 2.2634 |  | 18.5332
01/28 09:00:00 | 20.8848 | 20.7279 | 20.2153 | 21.0399 | 20.7846 | 21.0796 | 20.819 | 36.862 | 54.1034 | 27.1264 | 57.5713 | 59.0888 | 58.5194 | 81.8136 | [14 empty] | 0.0043352 |  | 2020.6429 |  |  |  | 767.8553 |  | 2990.6893 |  | 587.6904 |  | 516.417 |  | 542.6205
01/28 10:00:00 | 20.9007 | 21.5992 | 20.111 | 21.3893 | 21.0557 | 21.6097 | 21.9069 | 42.2823 | 51.0086 | 50.9916 | 58.7095 | 59.8726 | 58.7735 | 66.6189 | [14 empty] | 1.0124 |  | 592.2726 |  |  |  | 243.6809 |  | 244.2118 |  | 62.5583 |  | 45.5127 |  | 61.5499
01/28 11:00:00 | 20.8871 | 22.6677 | 20.3661 | 22.2123 | 21.7663 | 22.4095 | 22.7624 | 46.2177 | 44.4613 | 53.5973 | 51.0261 | 51.2822 | 50.8398 | 48.7753 | [14 empty] | 3.5169 |  | 6.5411 |  |  |  | 18.6103 |  | 23.2517 |  | 5.0661 |  | 6.2844 |  | 4.2624
01/28 12:00:00 | 20.9192 | 23.3914 | 20.9951 | 22.8346 | 22.4025 | 22.9868 | 22.9765 | 54.6244 | 40.5515 | 53.2318 | 45.5319 | 47.4313 | 45.1334 | 23.1394 | [14 empty] | 4.2326 |  | 991.3036 |  |  |  | 303.1813 |  | 905.5523 |  | 501.4225 |  | 590.0953 |  | 483.7356
01/28 13:00:00 | 21.1472 | 23.6518 | 21.8961 | 23.0481 | 22.7131 | 23.2082 | 22.8288 | 53.5512 | 37.5108 | 46.1475 | 41.7148 | 43.0081 | 41.2708 | 29.5493 | [14 empty] | 2.8278 |  | 576.0921 |  |  |  | 63.3844 |  | 275.4987 |  | 147.9996 |  | 181.1386 |  | 137.3925
01/28 14:00:00 | 21.5185 | 23.8343 | 22.7408 | 23.1103 | 22.903 | 23.3481 | 22.7088 | 52.9893 | 34.5638 | 41.5463 | 38.2739 | 38.7955 | 37.8672 | 36.3694 | [14 empty] | 1.4169 |  | 276.2199 |  |  |  | 3.2602 |  | 26.8004 |  | 3.6272 |  | 5.886 |  | 2.2432
01/28 15:00:00 | 22.0418 | 24.0513 | 23.106 | 23.1748 | 23.0727 | 23.4975 | 22.7409 | 48.864 | 32.4119 | 38.9222 | 35.9745 | 36.6131 | 35.6116 | 34.9266 | [14 empty] | 0.48872 |  | 194.2523 |  |  |  | 6.3236 |  | 15.9655 |  | 1.0981 |  | 2.8443 |  | 0.46931
01/28 16:00:00 | 22.417 | 24.1422 | 23.2249 | 23.1792 | 23.1241 | 23.5486 | 22.7222 | 44.7867 | 30.6057 | 36.5934 | 33.7298 | 34.3748 | 33.378 | 51.7349 | [14 empty] | 0.093168 |  | 48.2774 |  |  |  | 446.442 |  | 229.2639 |  | 324.1804 |  | 301.3702 |  | 336.9732
01/28 17:00:00 | 22.5097 | 24.1335 | 23.2498 | 23.095 | 23.0893 | 23.5033 | 22.8353 | 42.4488 | 28.7553 | 34.091 | 31.2328 | 31.7693 | 30.9269 | 18.0924 | [14 empty] | 0.10602 |  | 593.2346 |  |  |  | 113.698 |  | 255.9553 |  | 172.6709 |  | 187.0584 |  | 164.7241
01/28 18:00:00 | 22.5243 | 24.0622 | 23.2207 | 22.9425 | 22.9889 | 23.3922 | 22.7729 | 41.5927 | 27.1835 | 32.232 | 29.5882 | 30.0695 | 29.2283 | 51.1522 | [14 empty] | 0.061829 |  | 91.3832 |  |  |  | 574.4966 |  | 357.976 |  | 465.0056 |  | 444.482 |  | 480.6594
01/28 19:00:00 | 22.4852 | 23.8796 | 23.1124 | 22.7178 | 22.7921 | 23.1734 | 22.7877 | 41.6656 | 25.9178 | 30.4852 | 28.1257 | 28.566 | 27.86 | 51.3005 | [14 empty] | 0.09151 |  | 92.8314 |  |  |  | 644.2778 |  | 433.2759 |  | 537.0689 |  | 516.8554 |  | 549.4543
01/28 20:00:00 | 22.4322 | 23.648 | 22.9634 | 22.4373 | 22.5397 | 22.9063 | 22.8914 | 30.3179 | 19.0204 | 23.1222 | 21.8328 | 21.9675 | 21.5954 | 5.7893 | [14 empty] | 0.21088 |  | 601.6538 |  |  |  | 175.063 |  | 300.4291 |  | 257.3963 |  | 261.7365 |  | 249.834
01/28 21:00:00 | 22.3297 | 23.363 | 22.7975 | 22.1323 | 22.1725 | 22.5896 | 22.358 | 27.4533 | 18.3934 | 22.0629 | 20.769 | 20.9894 | 20.5944 | 15.6809 | [14 empty] | 0.00080157 |  | 138.5872 |  |  |  | 7.3576 |  | 40.7289 |  | 25.8878 |  | 28.1794 |  | 24.142
01/28 22:00:00 | 22.238 | 23.0078 | 22.6099 | 21.7879 | 21.706 | 22.1962 | 21.891 | 25.4136 | 17.7195 | 21.0455 | 19.7563 | 19.9711 | 19.5898 | 21.8136 | [14 empty] | 0.12044 |  | 12.9601 |  |  |  | 16.7615 |  | 0.5899 |  | 4.2325 |  | 3.3948 |  | 4.9449
01/28 23:00:00 | 22.1322 | 22.6495 | 22.4111 | 21.385 | 21.2671 | 21.807 | 21.5976 | 24.7478 | 17.1223 | 20.2028 | 19.0558 | 19.2728 | 18.8646 | 23.8709 | [14 empty] | 0.28571 |  | 0.76898 |  |  |  | 45.5438 |  | 13.455 |  | 23.1852 |  | 21.1422 |  | 25.0632
01/28 24:00:00 | 22.0036 | 22.2779 | 22.1833 | 21.0459 | 20.8813 | 21.4071 | 21.3659 | 28.8172 | 16.5999 | 19.3971 | 18.2638 | 18.4908 | 18.1265 | 25.8401 | [14 empty] | 0.40667 |  | 8.8632 |  |  |  | 85.3811 |  | 41.5126 |  | 57.3997 |  | 54.0115 |  | 59.5003
01/29 01:00:00 | 21.8643 | 21.9479 | 21.9284 | 20.682 | 20.4514 | 21.0515 | 21.0942 | 27.3777 | 16.1591 | 18.8719 | 17.9058 | 38.4129 | 17.7811 | 27.6126 | [14 empty] | 0.59314 |  | 0.05516 |  |  |  | 131.183 |  | 76.4006 |  | 94.2218 |  | 116.6466 |  | 96.6581
01/29 02:00:00 | 21.6257 | 21.5929 | 21.6363 | 20.2764 | 20.226 | 20.6585 | 20.9113 | 25.7564 | 15.6312 | 18.057 | 33.4467 | 46.5574 | 16.8877 | 28.4751 | [14 empty] | 0.51039 |  | 7.3916 |  |  |  | 164.9659 |  | 108.5374 |  | 24.7164 |  | 326.9701 |  | 134.2681
01/29 03:00:00 | 21.3683 | 21.2949 | 21.3379 | 20.0853 | 20.4495 | 20.2599 | 20.8126 | 24.9953 | 15.1817 | 17.5562 | 45.26 | 45.9811 | 34.1623 | 29.9152 | [14 empty] | 0.30876 |  | 24.2057 |  |  |  | 217.0784 |  | 152.7457 |  | 235.462 |  | 258.1125 |  | 18.0372
01/29 04:00:00 | 21.1046 | 21.0207 | 21.0441 | 20.2733 | 20.7334 | 20.0902 | 20.7443 | 23.7579 | 14.6985 | 16.8659 | 45.4073 | 39.6257 | 45.5697 | 29.6261 | [14 empty] | 0.12978 |  | 34.4359 |  |  |  | 222.8337 |  | 162.8244 |  | 249.045 |  | 99.9922 |  | 254.1989
01/29 05:00:00 | 20.8438 | 20.7439 | 20.7593 | 20.5601 | 20.9332 | 20.3057 | 20.7127 | 22.2753 | 14.1293 | 16.0212 | 39.1679 | 35.2685 | 44.9489 | 29.2176 | [14 empty] | 0.017178 |  | 48.1952 |  |  |  | 227.6572 |  | 174.1445 |  | 99.0087 |  | 36.6137 |  | 247.473
01/29 06:00:00 | 20.5874 | 20.465 | 20.4839 | 20.8048 | 20.9772 | 20.623 | 20.6752 | 20.9703 | 28.8728 | 29.1461 | 35.0431 | 33.5273 | 38.4709 | 29.438 | [14 empty] | 0.0077045 |  | 71.7016 |  |  |  | 0.3195 |  | 0.08519 |  | 31.4175 |  | 16.7223 |  | 81.5942
01/29 07:00:00 | 20.3299 | 20.3092 | 20.3597 | 20.8925 | 20.9335 | 20.8973 | 20.6481 | 32.3296 | 39.1206 | 39.9272 | 33.9289 | 32.2127 | 34.9991 | 29.9668 | [14 empty] | 0.10131 |  | 5.5828 |  |  |  | 83.7923 |  | 99.2098 |  | 15.6984 |  | 5.044 |  | 25.3238
01/29 08:00:00 | 20.2028 | 20.4591 | 20.5914 | 20.8821 | 20.8225 | 21.0012 | 20.6035 | 34.4681 | 38.8273 | 33.9922 | 32.6747 | 31.0435 | 34.0536 | 30.5753 | [14 empty] | 0.16054 |  | 15.1538 |  |  |  | 68.0949 |  | 11.6749 |  | 4.4075 |  | 0.21914 |  | 12.0987
01/29 09:00:00 | 20.2305 | 20.7021 | 20.8504 | 20.7893 | 20.6484 | 20.9912 | 20.9877 | 46.0919 | 54.1933 | 47.1186 | 56.1746 | 58.4955 | 57.9094 | 81.7785 | [14 empty] | 0.57338 |  | 1273.5327 |  |  |  | 760.9459 |  | 1201.3087 |  | 655.5594 |  | 542.1004 |  | 569.7325
01/29 10:00:00 | 20.2908 | 21.5978 | 21.0394 | 20.9305 | 20.7947 | 21.3452 | 22.144 | 47.6776 | 51.1797 | 53.3057 | 59.1989 | 60.2554 | 59.1253 | 64.5942 | [14 empty] | 3.4345 |  | 286.1735 |  |  |  | 179.9483 |  | 127.4314 |  | 29.1098 |  | 18.8258 |  | 29.9096
01/29 11:00:00 | 20.371 | 22.6603 | 21.616 | 21.7074 | 21.5249 | 22.1432 | 23.0166 | 54.4144 | 43.9583 | 52.4097 | 49.2222 | 58.0598 | 48.7474 | 19.7985 | [14 empty] | 6.999 |  | 1198.2583 |  |  |  | 583.6938 |  | 1063.4856 |  | 865.7529 |  | 1463.926 |  | 838.0338
01/29 12:00:00 | 20.7447 | 23.4292 | 22.4516 | 22.5255 | 22.3931 | 22.9153 | 22.9664 | 53.0184 | 39.7919 | 46.1763 | 44.8039 | 48.6485 | 42.8921 | 28.8246 | [14 empty] | 4.9359 |  | 585.3364 |  |  |  | 120.2802 |  | 301.0801 |  | 255.336 |  | 392.986 |  | 197.8948
01/29 13:00:00 | 21.2672 | 23.8161 | 23.0253 | 22.8521 | 23.1194 | 23.2822 | 22.9877 | 52.1245 | 37.0775 | 41.5047 | 41.0293 | 43.033 | 39.4254 | 22.8908 | [14 empty] | 2.9601 |  | 854.6102 |  |  |  | 201.2633 |  | 346.4757 |  | 329.0041 |  | 405.7072 |  | 273.3917
01/29 14:00:00 | 21.7556 | 24.0025 | 23.2895 | 22.9895 | 23.4109 | 23.4238 | 22.84 | 47.1696 | 34.1306 | 38.4513 | 37.4872 | 40.0569 | 36.4846 | 28.8985 | [14 empty] | 1.1759 |  | 333.8299 |  |  |  | 27.3746 |  | 91.2547 |  | 73.7644 |  | 124.5089 |  | 57.5486
01/29 15:00:00 | 22.2616 | 24.1771 | 23.4326 | 23.0597 | 23.5483 | 23.5221 | 22.8116 | 43.3358 | 32.048 | 35.9008 | 34.9194 | 37.3242 | 33.9546 | 27.9709 | [14 empty] | 0.30248 |  | 236.0814 |  |  |  | 16.6224 |  | 62.8837 |  | 48.2818 |  | 87.4837 |  | 35.8048
01/29 16:00:00 | 22.473 | 24.2606 | 23.4821 | 23.0554 | 23.5906 | 23.5479 | 22.664 | 41.2141 | 30.0063 | 28.6075 | 32.5169 | 34.7172 | 31.5913 | 30.2483 | [14 empty] | 0.03647 |  | 120.2471 |  |  |  | 0.058567 |  | 2.6923 |  | 5.1464 |  | 19.9705 |  | 1.8034
01/29 17:00:00 | 22.495 | 24.2661 | 23.4339 | 23.008 | 23.575 | 23.5234 | 22.6779 | 41.3984 | 28.5331 | 33.1101 | 31.4896 | 33.4962 | 30.6382 | 34.3465 | [14 empty] | 0.033456 |  | 49.729 |  |  |  | 33.7955 |  | 1.5286 |  | 8.1617 |  | 0.72297 |  | 13.7512
01/29 18:00:00 | 22.4535 | 24.185 | 23.3707 | 22.8641 | 23.4639 | 23.4002 | 22.6579 | 41.1641 | 27.1218 | 30.7995 | 29.4727 | 31.2863 | 28.6764 | 58.3861 | [14 empty] | 0.041806 |  | 296.5989 |  |  |  | 977.4585 |  | 761.0225 |  | 835.9876 |  | 734.3983 |  | 882.6651
01/29 19:00:00 | 22.395 | 23.9571 | 23.209 | 22.5919 | 23.2289 | 23.1179 | 22.8263 | 35.5484 | 25.7459 | 28.6836 | 27.876 | 28.9524 | 26.6721 | 19.7502 | [14 empty] | 0.18598 |  | 249.584 |  |  |  | 35.9489 |  | 79.8066 |  | 66.0292 |  | 84.6817 |  | 47.9128
01/29 20:00:00 | 22.2746 | 23.6869 | 23.0146 | 22.2904 | 22.9146 | 22.8156 | 22.4556 | 28.9391 | 18.7176 | 21.4158 | 21.4081 | 21.7134 | 20.144 | 9.1035 | [14 empty] | 0.032776 |  | 393.4509 |  |  |  | 92.4315 |  | 151.5935 |  | 151.4035 |  | 159.0103 |  | 121.8923
01/29 21:00:00 | 22.1839 | 23.412 | 22.814 | 22.0262 | 22.533 | 22.4938 | 21.8878 | 27.1629 | 18.2594 | 21.0091 | 20.6716 | 21.6271 | 20.0827 | 21.6781 | [14 empty] | 0.087703 |  | 30.0825 |  |  |  | 11.688 |  | 0.44759 |  | 1.0132 |  | 0.0026076 |  | 2.5454
01/29 22:00:00 | 22.0802 | 23.0637 | 22.5888 | 21.664 | 22.0286 | 22.0564 | 21.5079 | 26.0269 | 17.8664 | 20.5433 | 20.5983 | 21.4036 | 19.8962 | 24.9393 | [14 empty] | 0.32752 |  | 1.183 |  |  |  | 50.0255 |  | 19.3247 |  | 18.844 |  | 12.5013 |  | 25.4325
01/29 23:00:00 | 21.9583 | 22.6324 | 22.3421 | 21.2118 | 21.54 | 21.6179 | 21.2446 | 23.8323 | 17.1659 | 19.219 | 18.8851 | 19.64 | 18.2285 | 25.8311 | [14 empty] | 0.50938 |  | 3.9952 |  |  |  | 75.0857 |  | 43.7203 |  | 48.2462 |  | 38.3301 |  | 57.7988
01/29 24:00:00 | 21.8235 | 22.2815 | 22.0923 | 20.8555 | 21.1315 | 21.2634 | 21.0644 | 22.9009 | 16.4555 | 18.3296 | 18.0057 | 18.7218 | 17.386 | 27.5655 | [14 empty] | 0.57614 |  | 21.7588 |  |  |  | 123.4328 |  | 85.3019 |  | 91.3897 |  | 78.2122 |  | 103.6235
01/30 01:00:00 | 21.6759 | 21.9421 | 21.8361 | 20.5037 | 20.7106 | 20.9134 | 20.9518 | 22.0886 | 15.8538 | 17.609 | 17.2918 | 18.0246 | 16.713 | 27.9381 | [14 empty] | 0.52437 |  | 34.2171 |  |  |  | 146.0321 |  | 106.692 |  | 113.3455 |  | 98.279 |  | 126.0043
01/30 02:00:00 | 21.5452 | 21.696 | 21.6113 | 20.2512 | 20.3976 | 20.661 | 20.8604 | 20.9869 | 15.2521 | 16.8033 | 32.2139 | 36.5829 | 15.8661 | 29.2323 | [14 empty] | 0.46896 |  | 67.9874 |  |  |  | 195.4462 |  | 154.4794 |  | 8.8901 |  | 54.0305 |  | 178.6572
01/30 03:00:00 | 21.3983 | 21.4757 | 21.3899 | 20.162 | 20.2802 | 20.4256 | 20.7099 | 20.2847 | 14.72 | 16.179 | 43.1338 | 44.0069 | 32.2833 | 30.7111 | [14 empty] | 0.47379 |  | 108.7103 |  |  |  | 255.7141 |  | 211.1822 |  | 154.3229 |  | 176.7783 |  | 2.4716
01/30 04:00:00 | 21.24 | 21.2407 | 21.1578 | 20.3939 | 20.5307 | 20.3217 | 20.6513 | 19.6505 | 14.2538 | 15.6395 | 43.3639 | 35.4487 | 43.6578 | 30.3441 | [14 empty] | 0.34657 |  | 114.3538 |  |  |  | 258.8986 |  | 216.2262 |  | 169.515 |  | 26.0568 |  | 177.2529
01/30 05:00:00 | 21.0671 | 20.9827 | 20.9074 | 20.6945 | 20.7567 | 20.5418 | 20.5075 | 19.0649 | 13.8419 | 15.1464 | 38.0193 | 30.8524 | 35.1107 | 31.9369 | [14 empty] | 0.31315 |  | 165.6888 |  |  |  | 327.4295 |  | 281.9224 |  | 36.9955 |  | 1.1762 |  | 10.0731
01/30 06:00:00 | 20.8812 | 20.7083 | 20.6417 | 20.9314 | 20.785 | 20.7817 | 20.3791 | 19.0574 | 13.5058 | 14.9129 | 35.0751 | 30.6771 | 30.9896 | 32.5675 | [14 empty] | 0.25215 |  | 182.523 |  |  |  | 363.3508 |  | 311.6866 |  | 6.2877 |  | 3.5736 |  | 2.4897
01/30 07:00:00 | 20.6911 | 20.4253 | 20.3698 | 20.9992 | 20.713 | 20.8349 | 20.3336 | 18.2139 | 28.6377 | 12.0704 | 33.5695 | 29.2221 | 30.0387 | 33.9769 | [14 empty] | 0.12779 |  | 248.4741 |  |  |  | 28.5076 |  | 479.8948 |  | 0.166 |  | 22.6086 |  | 15.5094
01/30 08:00:00 | 20.4967 | 20.2641 | 20.143 | 20.9744 | 20.5801 | 20.7977 | 20.6496 | 21.671 | 54.397 | 27.2731 | 55.0879 | 56.2242 | 54.909 | 80.9511 | [14 empty] | 0.023392 |  | 3514.1349 |  |  |  | 705.1205 |  | 2881.3284 |  | 668.9093 |  | 611.4233 |  | 678.1933
01/30 09:00:00 | 20.3171 | 20.783 | 20.0911 | 21.2767 | 20.8496 | 21.1676 | 21.6841 | 41.478 | 51.3357 | 51.9175 | 56.4762 | 57.8745 | 56.9504 | 66.6438 | [14 empty] | 1.8687 |  | 633.3145 |  |  |  | 234.336 |  | 216.863 |  | 103.3795 |  | 76.9 |  | 93.9609
01/30 10:00:00 | 20.4162 | 22.0837 | 20.7101 | 22.2992 | 21.7891 | 22.2396 | 22.5708 | 49.9191 | 42.2493 | 51.8308 | 48.7863 | 49.6374 | 48.6456 | 56.6658 | [14 empty] | 4.6426 |  | 45.5177 |  |  |  | 207.8348 |  | 23.3767 |  | 62.086 |  | 49.398 |  | 64.324
01/30 11:00:00 | 21.0209 | 23.6427 | 22.0767 | 23.4108 | 22.9499 | 23.4557 | 22.8921 | 51.269 | 37.3201 | 45.2514 | 43.7014 | 43.1195 | 42.6865 | 28.5263 | [14 empty] | 3.5012 |  | 517.2305 |  |  |  | 77.3311 |  | 279.7293 |  | 230.2839 |  | 212.96 |  | 200.5113
01/30 12:00:00 | 21.8448 | 24.4451 | 23.4637 | 24.0343 | 23.7377 | 24.153 | 22.84 | 47.3521 | 34.9533 | 40.4714 | 40.5009 | 39.7101 | 39.516 | 31.0946 | [14 empty] | 0.99052 |  | 264.3041 |  |  |  | 14.8895 |  | 87.9246 |  | 88.4772 |  | 74.2272 |  | 70.9197
01/30 13:00:00 | 22.3997 | 24.7437 | 24.0194 | 24.2465 | 24.016 | 24.4157 | 22.9057 | 43.9473 | 32.7927 | 37.3114 | 37.6002 | 36.9704 | 36.8835 | 29.2885 | [14 empty] | 0.25605 |  | 214.8799 |  |  |  | 12.2791 |  | 64.3657 |  | 69.0837 |  | 59.011 |  | 57.6843
01/30 14:00:00 | 22.6131 | 24.7785 | 24.0173 | 24.1604 | 23.9836 | 24.4046 | 22.6803 | 41.5378 | 29.7987 | 34.1333 | 33.6773 | 33.123 | 32.9669 | 35.9728 | [14 empty] | 0.0045077 |  | 30.9689 |  |  |  | 38.12 |  | 3.3839 |  | 5.2696 |  | 8.1214 |  | 9.0358
01/30 15:00:00 | 22.949 | 24.9086 | 24.0586 | 24.1528 | 24.0301 | 24.4893 | 22.6826 | 39.2127 | 28.0584 | 32.1357 | 32.0068 | 31.4609 | 31.2939 | 30.6431 | [14 empty] | 0.070971 |  | 73.4374 |  |  |  | 6.6809 |  | 2.2276 |  | 1.8596 |  | 0.66875 |  | 0.42351
01/30 16:00:00 | 23.3624 | 25.1973 | 24.3131 | 24.3126 | 24.2569 | 24.7377 | 22.5917 | 37.0881 | 26.6608 | 30.467 | 30.6644 | 30.1338 | 29.9662 | 58.2533 | [14 empty] | 0.59387 |  | 447.9656 |  |  |  | 998.0851 |  | 772.0784 |  | 761.1479 |  | 790.7052 |  | 800.1562
01/30 17:00:00 | 23.5496 | 25.3694 | 24.4689 | 24.3975 | 24.3591 | 24.8638 | 22.7389 | 35.123 | 25.1398 | 28.8576 | 28.8733 | 28.4202 | 28.2332 | 34.3921 | [14 empty] | 0.65726 |  | 0.53419 |  |  |  | 85.6055 |  | 30.6309 |  | 30.4569 |  | 35.6634 |  | 37.9325
01/30 18:00:00 | 23.5326 | 25.3502 | 24.4389 | 24.2868 | 24.2573 | 24.7855 | 22.808 | 34.55 | 24.5928 | 28.2251 | 28.4028 | 27.962 | 27.8521 | 41.0507 | [14 empty] | 0.52516 |  | 42.2583 |  |  |  | 270.8625 |  | 164.4963 |  | 159.969 |  | 171.3125 |  | 174.203
01/30 19:00:00 | 23.2465 | 24.9952 | 24.0869 | 23.8051 | 23.7912 | 24.3317 | 22.7286 | 32.7074 | 23.8738 | 27.0669 | 27.0281 | 26.6178 | 26.4919 | 58.5335 | [14 empty] | 0.26825 |  | 666.9848 |  |  |  | 1201.2906 |  | 990.1416 |  | 992.59 |  | 1018.6087 |  | 1026.6631
01/30 20:00:00 | 22.7279 | 24.3615 | 23.5215 | 23.0899 | 23.0865 | 23.6343 | 22.8115 | 30.8182 | 22.9062 | 25.667 | 25.5396 | 25.1102 | 24.9929 | 41.6566 | [14 empty] | 0.0069922 |  | 117.4705 |  |  |  | 351.5802 |  | 255.6688 |  | 259.7597 |  | 273.7831 |  | 277.6804
01/30 21:00:00 | 22.1979 | 23.8072 | 22.9884 | 22.5164 | 22.405 | 22.9543 | 22.6453 | 24.4077 | 16.9889 | 19.5639 | 20.0144 | 19.6673 | 19.662 | 5.2341 | [14 empty] | 0.20016 |  | 367.6272 |  |  |  | 138.1746 |  | 205.3427 |  | 218.4559 |  | 208.315 |  | 208.1626
01/30 22:00:00 | 21.799 | 23.2876 | 22.5877 | 21.9785 | 21.7764 | 22.3271 | 21.9143 | 23.2543 | 16.5381 | 18.8316 | 19.1744 | 18.9019 | 18.8956 | 23.4815 | [14 empty] | 0.013309 |  | 0.05162 |  |  |  | 48.2116 |  | 21.6214 |  | 18.5515 |  | 20.9725 |  | 21.0303
01/30 23:00:00 | 21.4487 | 22.7381 | 22.2256 | 21.4229 | 21.1514 | 21.7407 | 21.3906 | 22.6916 | 16.1686 | 18.382 | 18.7777 | 18.5304 | 18.5026 | 25.9125 | [14 empty] | 0.0033822 |  | 10.3742 |  |  |  | 94.9428 |  | 56.7091 |  | 50.9055 |  | 54.4947 |  | 54.9065
01/30 24:00:00 | 21.0623 | 22.1259 | 21.8273 | 20.8025 | 20.4758 | 21.1835 | 21.1573 | 21.6716 | 15.7571 | 17.6998 | 18.1238 | 39.5954 | 17.8445 | 26.2247 | [14 empty] | 0.009028 |  | 20.731 |  |  |  | 109.5697 |  | 72.6733 |  | 65.6247 |  | 178.7763 |  | 70.2272
01/31 01:00:00 | 20.7052 | 21.6672 | 21.4605 | 20.3494 | 20.1785 | 20.6745 | 20.8872 | 20.5488 | 15.216 | 16.9384 | 36.5464 | 46.7734 | 16.9989 | 29.2936 | [14 empty] | 0.033114 |  | 76.4704 |  |  |  | 198.1783 |  | 152.6499 |  | 52.6032 |  | 305.5455 |  | 151.1586
01/31 02:00:00 | 20.428 | 21.2915 | 21.1772 | 20.1492 | 20.4989 | 20.3569 | 20.6672 | 32.1693 | 14.7128 | 16.3434 | 45.4178 | 45.65 | 36.8956 | 31.0946 | [14 empty] | 0.057245 |  | 1.1551 |  |  |  | 268.3631 |  | 217.5971 |  | 205.1555 |  | 211.8612 |  | 33.652
01/31 03:00:00 | 20.2799 | 20.9942 | 20.8857 | 20.4121 | 20.8718 | 20.2167 | 20.6222 | 34.927 | 14.366 | 16.0113 | 45.5538 | 39.7722 | 45.6192 | 31.4139 | [14 empty] | 0.11719 |  | 12.342 |  |  |  | 290.6301 |  | 237.2393 |  | 199.938 |  | 69.8619 |  | 201.7903
01/31 04:00:00 | 20.3054 | 20.7145 | 20.5922 | 20.7151 | 21.0743 | 20.4347 | 20.4997 | 38.2696 | 14.0077 | 15.6061 | 40.2817 | 36.342 | 46.0782 | 32.5873 | [14 empty] | 0.037769 |  | 32.2882 |  |  |  | 345.2003 |  | 288.3595 |  | 59.2042 |  | 14.0981 |  | 182.0052
01/31 05:00:00 | 20.3784 | 20.4329 | 20.3068 | 20.9252 | 21.0771 | 20.7261 | 20.418 | 39.4496 | 29.1862 | 12.8465 | 36.603 | 35.0231 | 40.032 | 33.8677 | [14 empty] | 0.0015718 |  | 31.1573 |  |  |  | 21.9165 |  | 441.8887 |  | 7.4821 |  | 1.3349 |  | 37.9982
01/31 06:00:00 | 20.4604 | 20.2738 | 20.0751 | 20.9748 | 20.9933 | 20.9705 | 20.4922 | 40.9208 | 39.7429 | 22.448 | 35.9597 | 34.1596 | 37.0699 | 33.1228 | [14 empty] | 0.0010117 |  | 60.8076 |  |  |  | 43.8259 |  | 113.9523 |  | 8.0479 |  | 1.0749 |  | 15.5791
01/31 07:00:00 | 20.5451 | 20.434 | 20.0092 | 20.9387 | 20.8547 | 21.0559 | 20.5268 | 42.7611 | 39.3421 | 41.5801 | 29.4547 | 28.6834 | 31.0252 | 30.5445 | [14 empty] | 0.00033505 |  | 149.2453 |  |  |  | 77.3964 |  | 121.7844 |  | 1.1877 |  | 3.464 |  | 0.23099
01/31 08:00:00 | 20.6602 | 20.7166 | 20.2687 | 20.8445 | 20.7079 | 21.0348 | 20.8817 | 45.887 | 54.2516 | 53.8452 | 57.3242 | 59.365 | 58.8729 | 75.0071 | [14 empty] | 0.049064 |  | 847.9829 |  |  |  | 430.7928 |  | 447.8265 |  | 312.6855 |  | 244.6777 |  | 260.3127
01/31 09:00:00 | 20.7849 | 21.8208 | 20.8824 | 21.1777 | 21.0831 | 21.6238 | 21.8942 | 53.3344 | 43.4945 | 53.6412 | 59.3844 | 60.7044 | 59.0762 | 62.6305 | [14 empty] | 1.2305 |  | 86.4169 |  |  |  | 366.1863 |  | 80.807 |  | 10.5375 |  | 3.7098 |  | 12.6328
01/31 10:00:00 | 21.2558 | 23.2863 | 22.0666 | 22.3593 | 22.1536 | 22.7771 | 22.7346 | 53.7177 | 38.816 | 46.2077 | 48.0715 | 47.7717 | 48.0048 | 48.0877 | [14 empty] | 2.1868 |  | 31.6968 |  |  |  | 85.9645 |  | 3.5342 |  | 0.00026257 |  | 0.099823 |  | 0.0068618
01/31 11:00:00 | 22.1155 | 24.1895 | 23.3716 | 23.7561 | 23.4866 | 23.9719 | 23.0114 | 48.9402 | 36.1043 | 41.8755 | 43.4237 | 42.4823 | 42.9588 | 12.3344 | [14 empty] | 0.80273 |  | 1339.981 |  |  |  | 565.0082 |  | 872.6733 |  | 966.5434 |  | 908.8923 |  | 937.8521
01/31 12:00:00 | 22.9304 | 24.7587 | 24.1474 | 24.4069 | 24.2385 | 24.6247 | 22.7799 | 44.2692 | 33.4723 | 38.6736 | 40.1539 | 39.4576 | 39.7353 | 32.4166 | [14 empty] | 0.022644 |  | 140.4846 |  |  |  | 1.1147 |  | 39.1509 |  | 59.8671 |  | 49.5762 |  | 53.5636
01/31 13:00:00 | 23.4556 | 25.1672 | 24.6106 | 24.6827 | 24.5592 | 24.9734 | 22.8509 | 41.4079 | 31.52 | 36.1023 | 37.1964 | 36.6397 | 37.485 | 39.602 | [14 empty] | 0.3657 |  | 3.2611 |  |  |  | 65.3193 |  | 12.248 |  | 5.7872 |  | 8.7757 |  | 4.4819
01/31 14:00:00 | 23.5464 | 25.2494 | 24.6566 | 24.6253 | 24.5329 | 24.9694 | 22.7812 | 38.712 | 29.6738 | 28.924 | 34.6656 | 34.2106 | 34.9403 | 34.4474 | [14 empty] | 0.58556 |  | 18.1861 |  |  |  | 22.7875 |  | 30.5089 |  | 0.047587 |  | 0.056076 |  | 0.24287
01/31 15:00:00 | 23.5451 | 25.2658 | 24.596 | 24.541 | 24.4657 | 24.9518 | 22.8689 | 36.5631 | 27.8991 | 32.6613 | 32.5843 | 32.16 | 32.7056 | 28.0451 | [14 empty] | 0.45717 |  | 72.5568 |  |  |  | 0.021313 |  | 21.3091 |  | 20.6043 |  | 16.9324 |  | 21.7206
01/31 16:00:00 | 23.6995 | 25.4272 | 24.7961 | 24.625 | 24.5631 | 25.0728 | 22.9154 | 29.4968 | 26.2989 | 25.7286 | 30.4685 | 30.097 | 30.5977 | 22.194 | [14 empty] | 0.61489 |  | 53.3307 |  |  |  | 16.8502 |  | 12.4937 |  | 68.4679 |  | 62.458 |  | 70.6221
01/31 17:00:00 | 23.7449 | 25.5521 | 24.8728 | 24.6613 | 24.6169 | 25.1471 | 22.7808 | 32.3481 | 24.5639 | 28.6509 | 27.9015 | 27.5838 | 28.0001 | 25.755 | [14 empty] | 0.92957 |  | 43.4687 |  |  |  | 1.4188 |  | 8.3861 |  | 4.6075 |  | 3.3446 |  | 5.0406
01/31 18:00:00 | 23.696 | 25.5172 | 24.8083 | 24.5393 | 24.5112 | 25.0552 | 22.7961 | 28.9111 | 22.8034 | 25.6908 | 25.1365 | 24.8003 | 25.1625 | 41.7648 | [14 empty] | 0.80978 |  | 165.2163 |  |  |  | 359.5333 |  | 258.3718 |  | 276.4974 |  | 287.794 |  | 275.635
01/31 19:00:00 | 23.5711 | 25.3891 | 24.6659 | 24.2961 | 24.2861 | 24.8463 | 22.7642 | 28.4129 | 21.8536 | 24.8912 | 24.6677 | 24.2905 | 24.6724 | 32.9857 | [14 empty] | 0.65114 |  | 20.9106 |  |  |  | 123.9232 |  | 65.5211 |  | 69.1879 |  | 75.606 |  | 69.1109
01/31 20:00:00 | 23.2213 | 25.0856 | 24.293 | 23.8172 | 23.8087 | 24.3891 | 22.8515 | 27.6529 | 21.0857 | 24.0606 | 24.0224 | 23.7085 | 24.0562 | 23.3948 | [14 empty] | 0.13672 |  | 18.1314 |  |  |  | 5.3317 |  | 0.44332 |  | 0.39389 |  | 0.098428 |  | 0.43746
01/31 21:00:00 | 22.7769 | 24.7327 | 23.9103 | 23.3974 | 23.2945 | 23.8857 | 22.5627 | 21.6949 | 15.5062 | 18.2818 | 18.5725 | 18.3043 | 18.6189 | 11.9399 | [14 empty] | 0.045886 |  | 95.1597 |  |  |  | 12.7184 |  | 40.2188 |  | 43.9915 |  | 40.5054 |  | 44.6085
01/31 22:00:00 | 22.4667 | 24.3917 | 23.6009 | 23.0465 | 22.8442 | 23.4424 | 22.0964 | 20.5476 | 15.0167 | 14.7073 | 17.6715 | 17.4168 | 17.7396 | 18.9188 | [14 empty] | 0.1371 |  | 2.6531 |  |  |  | 15.2264 |  | 17.7369 |  | 1.5559 |  | 2.256 |  | 1.3906
01/31 23:00:00 | 22.2005 | 24.0051 | 23.354 | 22.6611 | 22.3864 | 23.0282 | 21.8107 | 19.5689 | 14.5125 | 17.226 | 16.8321 | 16.6287 | 16.8865 | 21.4329 | [14 empty] | 0.15189 |  | 3.4744 |  |  |  | 47.891 |  | 17.6977 |  | 21.1672 |  | 23.0799 |  | 20.6698
01/31 24:00:00 | 21.9246 | 23.6427 | 23.1415 | 22.2268 | 21.9689 | 22.6421 | 21.632 | 18.4891 | 14.0281 | 16.1466 | 16.0118 | 15.8481 | 16.0534 | 22.6304 | [14 empty] | 0.085604 |  | 17.1504 |  |  |  | 73.998 |  | 42.0395 |  | 43.805 |  | 45.9986 |  | 43.2563
02/01 01:00:00 | 21.6628 | 23.3364 | 22.854 | 21.9098 | 21.5884 | 22.3435 | 21.4942 | 14.6973 | 13.4491 | 12.8869 | 15.1141 | 14.9707 | 15.1633 | 23.3967 | [14 empty] | 0.028418 |  | 75.6793 |  |  |  | 98.9548 |  | 110.4546 |  | 68.6004 |  | 70.9971 |  | 67.7886
02/01 02:00:00 | 21.4828 | 23.0708 | 22.6491 | 21.6581 | 21.3236 | 22.0987 | 21.3893 | 16.8335 | 12.9452 | 15.0683 | 14.2792 | 14.1577 | 14.3424 | 24.663 | [14 empty] | 0.0087389 |  | 61.3005 |  |  |  | 137.3056 |  | 92.0573 |  | 107.8215 |  | 110.3601 |  | 106.5142
02/01 03:00:00 | 21.3262 | 22.809 | 22.4647 | 21.4052 | 21.0751 | 21.8485 | 21.4047 | 15.7474 | 12.5188 | 14.1112 | 13.6365 | 13.5213 | 13.6611 | 23.5475 | [14 empty] | 0.0061708 |  | 60.8419 |  |  |  | 121.634 |  | 89.0453 |  | 98.2285 |  | 100.5262 |  | 97.741
02/01 04:00:00 | 21.1044 | 22.506 | 22.208 | 21.1089 | 20.7781 | 21.5499 | 21.3543 | 14.8167 | 12.0765 | 13.3806 | 12.8911 | 12.7835 | 12.9184 | 25.083 | [14 empty] | 0.062447 |  | 105.396 |  |  |  | 169.1675 |  | 136.9467 |  | 148.6417 |  | 151.2775 |  | 147.9775
02/01 05:00:00 | 20.8752 | 22.2088 | 21.9506 | 20.7484 | 20.4089 | 21.1861 | 21.2683 | 13.6413 | 11.5082 | 12.5556 | 11.8239 | 34.1533 | 11.8416 | 24.9503 | [14 empty] | 0.15447 |  | 127.8932 |  |  |  | 180.6886 |  | 153.6275 |  | 172.302 |  | 84.6949 |  | 171.8367
02/01 06:00:00 | 20.6103 | 21.8858 | 21.6567 | 20.3951 | 20.247 | 20.8313 | 21.1967 | 13.0434 | 11.1249 | 12.0258 | 28.9088 | 42.7672 | 11.3669 | 25.0675 | [14 empty] | 0.3439 |  | 144.5776 |  |  |  | 194.3951 |  | 170.0857 |  | 14.7562 |  | 313.2791 |  | 187.7049
02/01 07:00:00 | 20.3478 | 21.5825 | 21.3728 | 20.2698 | 20.539 | 20.5497 | 21.1495 | 27.0762 | 10.905 | 11.9101 | 42.2636 | 33.5863 | 11.4217 | 25.9834 | [14 empty] | 0.6427 |  | 1.1942 |  |  |  | 227.3579 |  | 198.0583 |  | 265.0461 |  | 57.8039 |  | 212.0429
02/01 08:00:00 | 20.262 | 21.3205 | 21.1233 | 20.5532 | 20.8427 | 20.2895 | 21.3661 | 47.6843 | 35.8279 | 13.0638 | 58.4769 | 55.51 | 39.6698 | 75.7668 | [14 empty] | 1.2192 |  | 788.6228 |  |  |  | 1595.1142 |  | 3931.6576 |  | 298.9388 |  | 410.3362 |  | 1302.9918
02/01 09:00:00 | 20.5701 | 21.225 | 20.9333 | 21.5387 | 21.5616 | 20.2298 | 22.2882 | 50.4594 | 52.8662 | 37.4686 | 54.2444 | 56.0199 | 58.9303 | 61.2462 | [14 empty] | 2.9517 |  | 116.3539 |  |  |  | 70.224 |  | 565.3756 |  | 49.0249 |  | 27.314 |  | 5.3633
02/01 10:00:00 | 21.2781 | 22.0597 | 21.0874 | 22.9964 | 22.7998 | 21.3476 | 22.9942 | 50.6985 | 39.3967 | 49.4664 | 46.3786 | 45.4086 | 54.5503 | 16.8892 | [14 empty] | 2.9451 |  | 1143.0653 |  |  |  | 506.5872 |  | 1061.2699 |  | 869.6223 |  | 813.3567 |  | 1418.3547
02/01 11:00:00 | 22.1976 | 23.7332 | 22.0064 | 24.0101 | 23.918 | 23.3159 | 22.8624 | 45.3431 | 32.8878 | 41.2153 | 41.8234 | 40.1862 | 43.3328 | 26.814 | [14 empty] | 0.44184 |  | 343.3274 |  |  |  | 36.8914 |  | 207.3989 |  | 225.2829 |  | 178.8154 |  | 272.8701
02/01 12:00:00 | 22.8392 | 24.7411 | 23.4404 | 24.473 | 24.4795 | 24.517 | 22.8714 | 41.273 | 31.1053 | 35.3192 | 39.3777 | 38.2701 | 38.7162 | 25.1072 | [14 empty] | 0.0010368 |  | 261.3325 |  |  |  | 35.9772 |  | 104.2841 |  | 203.6472 |  | 173.2621 |  | 185.205
02/01 13:00:00 | 23.2092 | 25.0474 | 24.216 | 24.696 | 24.6899 | 24.8991 | 22.8713 | 38.1451 | 28.9361 | 32.3747 | 36.1403 | 35.1338 | 35.8903 | 23.3471 | [14 empty] | 0.11415 |  | 218.9819 |  |  |  | 31.237 |  | 81.4972 |  | 163.6653 |  | 138.9254 |  | 157.3312
02/01 14:00:00 | 23.2973 | 25.051 | 24.2506 | 24.6903 | 24.67 | 24.8994 | 22.6617 | 35.6144 | 26.9927 | 30.3005 | 33.6275 | 32.663 | 33.701 | 26.7767 | [14 empty] | 0.40396 |  | 78.1037 |  |  |  | 0.046627 |  | 12.4171 |  | 46.9334 |  | 34.6485 |  | 47.9456
02/01 15:00:00 | 23.3882 | 25.0671 | 24.2453 | 24.7147 | 24.6809 | 24.9388 | 22.7564 | 33.9332 | 25.582 | 28.7846 | 31.776 | 30.8994 | 32.0759 | 24.7701 | [14 empty] | 0.39913 |  | 83.9626 |  |  |  | 0.65915 |  | 16.1167 |  | 49.0828 |  | 37.5679 |  | 53.3744
02/01 16:00:00 | 23.5602 | 25.2168 | 24.375 | 24.8587 | 24.8205 | 25.0759 | 22.8162 | 26.4258 | 24.0177 | 22.9351 | 29.5699 | 28.757 | 29.7918 | 23.4791 | [14 empty] | 0.55352 |  | 8.6828 |  |  |  | 0.29007 |  | 0.29602 |  | 37.0973 |  | 27.856 |  | 39.85
02/01 17:00:00 | 23.6198 | 25.3166 | 24.4296 | 24.9339 | 24.8915 | 25.1834 | 22.6917 | 29.8979 | 22.3553 | 25.6898 | 26.8934 | 26.1715 | 27.0024 | 24.2078 | [14 empty] | 0.86133 |  | 32.3777 |  |  |  | 3.4318 |  | 2.1965 |  | 7.2125 |  | 3.8563 |  | 7.8097
02/01 18:00:00 | 23.6032 | 25.2699 | 24.3932 | 24.8513 | 24.8141 | 25.1504 | 22.7017 | 27.3496 | 20.77 | 23.319 | 24.8661 | 24.2015 | 24.9446 | 42.0208 | [14 empty] | 0.81264 |  | 215.244 |  |  |  | 451.5971 |  | 349.7566 |  | 294.2844 |  | 317.5289 |  | 291.5979
02/01 19:00:00 | 23.5267 | 25.1487 | 24.2914 | 24.6589 | 24.6341 | 25.0149 | 22.7608 | 27.3052 | 20.2696 | 23.0884 | 24.7761 | 24.1922 | 24.869 | 20.0045 | [14 empty] | 0.58653 |  | 53.2992 |  |  |  | 0.070271 |  | 9.5102 |  | 22.7681 |  | 17.5368 |  | 23.6627
02/01 20:00:00 | 23.1701 | 24.7534 | 23.9111 | 24.117 | 24.1619 | 24.5801 | 22.7833 | 26.1361 | 19.6912 | 22.2419 | 23.8584 | 23.2035 | 23.8126 | 38.7708 | [14 empty] | 0.14961 |  | 159.6364 |  |  |  | 364.0326 |  | 273.2048 |  | 222.3791 |  | 242.3417 |  | 223.7481
02/01 21:00:00 | 22.7117 | 24.3295 | 23.437 | 23.5721 | 23.634 | 24.0689 | 22.6822 | 20.1826 | 14.374 | 16.5183 | 18.0354 | 17.4668 | 18.0072 | 9.3367 | [14 empty] | 0.00086978 |  | 117.6335 |  |  |  | 25.3744 |  | 51.575 |  | 75.6665 |  | 66.099 |  | 75.1774
02/01 22:00:00 | 22.3786 | 23.9061 | 23.0989 | 23.1017 | 23.1064 | 23.6002 | 22.1909 | 19.6649 | 14.1254 | 16.1515 | 17.6901 | 17.2198 | 17.676 | 18.6231 | [14 empty] | 0.035216 |  | 1.0854 |  |  |  | 20.2291 |  | 6.1087 |  | 0.87053 |  | 1.9693 |  | 0.89693
02/01 23:00:00 | 22.084 | 23.411 | 22.8053 | 22.6326 | 22.5073 | 23.1197 | 21.8745 | 19.5145 | 13.9111 | 15.958 | 17.5936 | 17.1538 | 17.5849 | 21.0896 | [14 empty] | 0.043895 |  | 2.4808 |  |  |  | 51.531 |  | 26.3334 |  | 12.2222 |  | 15.4905 |  | 12.2831
02/01 24:00:00 | 21.7742 | 22.9586 | 22.4949 | 22.2025 | 21.9816 | 22.6732 | 21.6286 | 18.3011 | 13.478 | 15.2043 | 16.6056 | 16.2591 | 16.6267 | 23.2695 | [14 empty] | 0.021201 |  | 24.6853 |  |  |  | 95.873 |  | 65.0477 |  | 44.4075 |  | 49.146 |  | 44.1262
02/02 01:00:00 | 21.4882 | 22.6245 | 22.2083 | 21.892 | 21.584 | 22.2773 | 21.425 | 17.7407 | 13.0706 | 12.2633 | 16.147 | 15.8046 | 16.1474 | 24.25 | [14 empty] | 0.0039878 |  | 42.3707 |  |  |  | 124.9795 |  | 143.681 |  | 65.6577 |  | 71.3248 |  | 65.6521
02/02 02:00:00 | 21.264 | 22.3565 | 22.0116 | 21.6316 | 21.2396 | 21.9972 | 21.2769 | 14.0265 | 12.6166 | 14.6194 | 15.4356 | 15.1323 | 15.4556 | 25.6045 | [14 empty] | 0.00016562 |  | 134.0497 |  |  |  | 168.6862 |  | 120.6722 |  | 103.4064 |  | 109.667 |  | 103
02/02 03:00:00 | 21.0672 | 22.09 | 21.8318 | 21.3622 | 20.9675 | 21.7323 | 21.1987 | 16.5163 | 12.199 | 13.6667 | 14.6743 | 14.3804 | 14.693 | 24.7463 | [14 empty] | 0.017277 |  | 67.7341 |  |  |  | 157.4346 |  | 122.7573 |  | 101.4467 |  | 107.4524 |  | 101.07
02/02 04:00:00 | 20.8918 | 21.8206 | 21.5848 | 21.0827 | 20.6964 | 21.4587 | 21.2011 | 13.3941 | 11.9235 | 11.2149 | 14.5756 | 14.3208 | 14.5433 | 25.6457 | [14 empty] | 0.095702 |  | 150.1002 |  |  |  | 188.2975 |  | 208.2467 |  | 122.5463 |  | 128.2532 |  | 123.2614
02/02 05:00:00 | 20.6797 | 21.5508 | 21.3776 | 20.7975 | 20.4164 | 21.1762 | 21.1184 | 13.467 | 11.6623 | 13.5719 | 14.3816 | 32.7894 | 14.3936 | 27.0441 | [14 empty] | 0.1924 |  | 184.3388 |  |  |  | 236.6017 |  | 181.5009 |  | 160.3395 |  | 33.0086 |  | 160.0358
02/02 06:00:00 | 20.5111 | 21.2606 | 21.1794 | 20.501 | 20.2738 | 20.8813 | 21.1223 | 12.8531 | 9.84 | 10.7413 | 12.1759 | 44.3974 | 12.2807 | 26.4715 | [14 empty] | 0.37354 |  | 185.4607 |  |  |  | 276.6052 |  | 247.4373 |  | 204.363 |  | 321.3379 |  | 201.3785
02/02 07:00:00 | 20.343 | 21.0351 | 20.9591 | 20.2645 | 20.4909 | 20.6471 | 21.016 | 12.2432 | 9.7306 | 10.4955 | 11.7495 | 43.5836 | 13.3314 | 26.5404 | [14 empty] | 0.45292 |  | 204.4102 |  |  |  | 282.5719 |  | 257.4402 |  | 218.7709 |  | 290.4687 |  | 174.478
02/02 08:00:00 | 20.1653 | 20.8682 | 20.7923 | 20.0842 | 20.8112 | 20.418 | 21.2957 | 25.6604 | 36.3359 | 34.2916 | 29.2472 | 60.3771 | 40.2631 | 80.5346 | [14 empty] | 1.2778 |  | 3011.1783 |  |  |  | 1953.5224 |  | 2138.4186 |  | 2630.3935 |  | 406.3265 |  | 1621.7907
02/02 09:00:00 | 20.0929 | 20.81 | 20.7467 | 20.0297 | 22.0693 | 20.3009 | 22.3676 | 50.4255 | 53.3922 | 50.6706 | 59.0291 | 48.4408 | 59.4642 | 62.5446 | [14 empty] | 5.1741 |  | 146.8735 |  |  |  | 83.7673 |  | 140.9926 |  | 12.3593 |  | 198.9177 |  | 9.4891
02/02 10:00:00 | 20.6062 | 21.6248 | 21.3656 | 20.8218 | 23.2154 | 21.3601 | 22.9386 | 48.8747 | 47.3666 | 48.8085 | 53.6133 | 40.5576 | 52.3522 | 15.9113 | [14 empty] | 5.44 |  | 1086.5865 |  |  |  | 989.4334 |  | 1082.2255 |  | 1421.4415 |  | 607.4364 |  | 1327.9375
02/02 11:00:00 | 21.7032 | 23.565 | 22.9902 | 22.7749 | 23.9443 | 23.4057 | 22.7779 | 43.4424 | 37.712 | 41.2256 | 43.5666 | 39.1205 | 42.5998 | 21.7246 | [14 empty] | 1.1549 |  | 471.6645 |  |  |  | 255.5985 |  | 380.2918 |  | 477.0727 |  | 302.6198 |  | 435.7743
02/02 12:00:00 | 22.5704 | 24.9749 | 24.2365 | 24.227 | 24.3464 | 24.7051 | 22.8762 | 39.7696 | 33.0649 | 36.6134 | 38.8972 | 36.0731 | 37.7575 | 32.2208 | [14 empty] | 0.093501 |  | 56.9844 |  |  |  | 0.71252 |  | 19.2945 |  | 44.5739 |  | 14.8403 |  | 30.6552
02/02 13:00:00 | 23.2458 | 25.5982 | 24.8358 | 24.7237 | 24.708 | 25.2116 | 22.7963 | 38.6743 | 32.5047 | 35.8691 | 38.3661 | 35.1036 | 37.7307 | 27.3116 | [14 empty] | 0.20205 |  | 129.1106 |  |  |  | 26.9685 |  | 73.2304 |  | 122.2017 |  | 60.716 |  | 108.5587
02/02 14:00:00 | 23.3474 | 25.646 | 24.8336 | 24.6315 | 24.6742 | 25.1216 | 22.9622 | 35.4249 | 29.6503 | 32.8301 | 34.9887 | 31.963 | 33.8504 | 25.0041 | [14 empty] | 0.14838 |  | 108.5942 |  |  |  | 21.5875 |  | 61.2463 |  | 99.692 |  | 48.4274 |  | 78.2571
02/02 15:00:00 | 23.3557 | 25.6919 | 24.8146 | 24.6044 | 24.654 | 25.1656 | 23.1587 | 32.3233 | 26.5697 | 29.7705 | 31.6421 | 28.9617 | 30.6684 | 22.5 | [14 empty] | 0.038819 |  | 96.4976 |  |  |  | 16.5623 |  | 52.8607 |  | 83.5785 |  | 41.754 |  | 66.7227
02/02 16:00:00 | 23.8398 | 26.1532 | 25.2538 | 24.995 | 25.038 | 25.576 | 23.3042 | 29.361 | 23.2177 | 26.8077 | 28.3289 | 26.0259 | 27.0122 | 22.652 | [14 empty] | 0.28677 |  | 45.011 |  |  |  | 0.31999 |  | 17.2702 |  | 32.2273 |  | 11.3833 |  | 19.0115
02/02 17:00:00 | 24.1496 | 26.5306 | 25.6095 | 25.3133 | 25.3258 | 25.9243 | 23.2605 | 27.1419 | 20.4529 | 24.5055 | 25.7358 | 23.5205 | 24.3214 | 26.6967 | [14 empty] | 0.79061 |  | 0.19818 |  |  |  | 38.9855 |  | 4.8014 |  | 0.92333 |  | 10.0881 |  | 5.6421
02/02 18:00:00 | 24.1912 | 26.636 | 25.7001 | 25.3474 | 25.3697 | 26.0076 | 22.8869 | 26.4178 | 22.1044 | 24.4116 | 25.4522 | 23.3154 | 24.9096 | 31.9076 | [14 empty] | 1.7011 |  | 30.1376 |  |  |  | 96.1037 |  | 56.19 |  | 41.6724 |  | 73.8256 |  | 48.9719
02/02 19:00:00 | 24.0491 | 26.463 | 25.5397 | 25.1449 | 25.1654 | 25.8014 | 22.6982 | 27.1721 | 24.1514 | 25.0098 | 26.1031 | 24.1289 | 26.3627 | 62.0115 | [14 empty] | 1.8248 |  | 1213.7861 |  |  |  | 1433.3869 |  | 1369.1233 |  | 1289.4159 |  | 1435.0957 |  | 1270.8395
02/02 20:00:00 | 23.4993 | 25.8926 | 24.9981 | 24.4266 | 24.4292 | 25.137 | 22.815 | 25.9426 | 23.1383 | 24.0985 | 24.9649 | 23.1396 | 25.0113 | 40.018 | [14 empty] | 0.46826 |  | 198.1166 |  |  |  | 284.9247 |  | 253.4289 |  | 226.5942 |  | 284.8792 |  | 225.2013
02/02 21:00:00 | 22.9471 | 25.3717 | 24.4595 | 23.8158 | 23.7185 | 24.556 | 22.641 | 20.848 | 17.091 | 18.5169 | 19.7026 | 18.3682 | 19.6655 | 5.0814 | [14 empty] | 0.093678 |  | 248.585 |  |  |  | 144.2285 |  | 180.5104 |  | 213.7791 |  | 176.5371 |  | 212.6955
02/02 22:00:00 | 22.5513 | 24.9125 | 24.0686 | 23.3347 | 23.118 | 24.0446 | 21.9431 | 20.3469 | 16.7654 | 18.1078 | 19.2996 | 18.053 | 19.3239 | 22.2963 | [14 empty] | 0.36998 |  | 3.8 |  |  |  | 30.5905 |  | 17.5437 |  | 8.9803 |  | 18.0052 |  | 8.835
02/02 23:00:00 | 22.1996 | 24.3992 | 23.7114 | 22.8148 | 22.5134 | 23.4449 | 21.4493 | 19.3719 | 16.3264 | 17.4275 | 18.3705 | 17.2553 | 18.3993 | 26.0197 | [14 empty] | 0.56297 |  | 44.1928 |  |  |  | 93.9593 |  | 73.8246 |  | 58.5101 |  | 76.8144 |  | 58.0695
02/02 24:00:00 | 21.811 | 23.8117 | 23.3099 | 22.2226 | 21.9329 | 22.8736 | 21.1013 | 19.2341 | 16.0349 | 17.1643 | 18.3911 | 17.2998 | 18.421 | 28.526 | [14 empty] | 0.50375 |  | 86.3395 |  |  |  | 156.0268 |  | 129.0882 |  | 102.7154 |  | 126.0274 |  | 102.1102
02/03 01:00:00 | 21.4286 | 23.3376 | 22.9124 | 21.7469 | 21.3609 | 22.4062 | 20.8554 | 19.5237 | 15.8564 | 17.1879 | 18.723 | 17.6664 | 18.7582 | 29.1122 | [14 empty] | 0.32863 |  | 91.9386 |  |  |  | 175.7152 |  | 142.1893 |  | 107.935 |  | 131.0048 |  | 107.2046
02/03 02:00:00 | 21.1087 | 22.9173 | 22.5789 | 21.3125 | 20.8442 | 21.9725 | 20.6653 | 18.6633 | 15.4537 | 16.6152 | 17.9495 | 17.0003 | 17.9753 | 30.7615 | [14 empty] | 0.1966 |  | 146.3656 |  |  |  | 234.3264 |  | 200.1164 |  | 164.1472 |  | 189.3695 |  | 163.4857
02/03 03:00:00 | 20.7947 | 22.5914 | 22.2507 | 20.8964 | 20.4461 | 21.5531 | 20.5545 | 17.464 | 14.9073 | 15.7852 | 16.808 | 37.9901 | 16.8486 | 31.9537 | [14 empty] | 0.057695 |  | 209.9518 |  |  |  | 290.5808 |  | 261.4206 |  | 229.3931 |  | 36.4381 |  | 228.1631
02/03 04:00:00 | 20.4813 | 22.2893 | 21.9221 | 20.5583 | 20.2385 | 21.2134 | 20.4089 | 30.0755 | 14.2718 | 14.8816 | 15.6217 | 46.4579 | 15.6434 | 32.5401 | [14 empty] | 0.0052448 |  | 6.0746 |  |  |  | 333.7327 |  | 311.8238 |  | 286.2331 |  | 193.7041 |  | 285.4981
02/03 05:00:00 | 20.3172 | 21.9799 | 21.5935 | 20.2347 | 20.5061 | 20.8887 | 20.262 | 42.0177 | 13.8268 | 14.4719 | 32.7956 | 36.3657 | 15.2688 | 33.8476 | [14 empty] | 0.0030439 |  | 66.7518 |  |  |  | 400.8314 |  | 375.4168 |  | 1.1066 |  | 6.3411 |  | 345.1694
02/03 06:00:00 | 20.5095 | 21.6536 | 21.2606 | 20.0498 | 20.7545 | 20.5442 | 20.1684 | 37.3785 | 13.5104 | 14.283 | 45.5048 | 32.0114 | 15.1873 | 35.06 | [14 empty] | 0.11633 |  | 5.3754 |  |  |  | 464.3847 |  | 431.681 |  | 109.0954 |  | 9.2936 |  | 394.9238
02/03 07:00:00 | 20.7356 | 21.3144 | 20.9223 | 20.2215 | 20.7503 | 20.1856 | 20.0505 | 27.3601 | 13.2644 | 13.9209 | 46.0364 | 31.3924 | 33.7395 | 35.2134 | [14 empty] | 0.4694 |  | 61.6736 |  |  |  | 481.7578 |  | 453.3695 |  | 117.1371 |  | 14.5998 |  | 2.1722
02/03 08:00:00 | 20.7192 | 20.9713 | 20.5844 | 20.4869 | 20.639 | 19.9807 | 20.2675 | 33.8737 | 37.9142 | 36.4688 | 62.6462 | 59.4361 | 63.7219 | 77.2013 | [14 empty] | 0.20405 |  | 1877.2863 |  |  |  | 1543.4793 |  | 1659.1362 |  | 211.8517 |  | 315.6055 |  | 181.6961
02/03 09:00:00 | 20.6465 | 20.7877 | 20.4224 | 21.346 | 20.8661 | 20.6843 | 21.2126 | 48.745 | 54.1657 | 52.4043 | 58.5892 | 60.6183 | 59.7201 | 70.8725 | [14 empty] | 0.32037 |  | 489.627 |  |  |  | 279.1159 |  | 341.0752 |  | 150.8781 |  | 105.1481 |  | 124.3757
02/03 10:00:00 | 20.8636 | 21.5213 | 21.0048 | 22.4255 | 21.8298 | 21.9774 | 22.1344 | 52.3115 | 49.3194 | 52.1869 | 51.5263 | 52.0956 | 51.7003 | 64.0801 | [14 empty] | 1.6149 |  | 138.5002 |  |  |  | 217.8802 |  | 141.4501 |  | 157.5989 |  | 143.6293 |  | 153.2604
02/03 11:00:00 | 21.5048 | 23.2184 | 22.3167 | 23.4608 | 23.1258 | 23.3222 | 22.8966 | 51.1807 | 38.7809 | 45.372 | 44.6905 | 43.5924 | 42.9849 | 30.0727 | [14 empty] | 1.9373 |  | 445.5496 |  |  |  | 75.8331 |  | 234.0681 |  | 213.6807 |  | 182.7821 |  | 166.7244
02/03 12:00:00 | 22.3907 | 24.6186 | 23.7342 | 24.1594 | 23.9869 | 24.2214 | 22.913 | 45.7908 | 33.8268 | 39.4897 | 40.1862 | 38.7191 | 38.165 | 30.0963 | [14 empty] | 0.27278 |  | 246.3169 |  |  |  | 13.9168 |  | 88.2361 |  | 101.8058 |  | 74.3528 |  | 65.1032
02/03 13:00:00 | 23.2507 | 25.2664 | 24.4545 | 24.5703 | 24.4089 | 24.772 | 22.8806 | 40.6901 | 31.5518 | 35.9815 | 36.7721 | 35.6436 | 35.0004 | 32.444 | [14 empty] | 0.13697 |  | 67.9973 |  |  |  | 0.79612 |  | 12.5139 |  | 18.7326 |  | 10.2376 |  | 6.5351
02/03 14:00:00 | 23.5532 | 25.4141 | 24.587 | 24.6506 | 24.5027 | 24.8815 | 22.8953 | 39.4406 | 29.8197 | 34.5405 | 35.7987 | 34.6872 | 33.9195 | 34.489 | [14 empty] | 0.4328 |  | 24.5186 |  |  |  | 21.8024 |  | 0.0026514 |  | 1.7153 |  | 0.039288 |  | 0.32433
02/03 15:00:00 | 23.6314 | 25.5047 | 24.6487 | 24.6818 | 24.5449 | 24.9643 | 22.8464 | 39.6061 | 28.8633 | 33.947 | 35.9301 | 34.7645 | 34.2897 | 34.7442 | [14 empty] | 0.6162 |  | 23.6388 |  |  |  | 34.5849 |  | 0.63553 |  | 1.4064 |  | 0.00041401 |  | 0.20651
02/03 16:00:00 | 23.7951 | 25.7377 | 24.8494 | 24.8337 | 24.7046 | 25.1835 | 22.7449 | 31.2825 | 27.5509 | 27.0594 | 33.1857 | 32.0743 | 31.9257 | 35.2149 | [14 empty] | 1.103 |  | 15.4635 |  |  |  | 58.736 |  | 66.5124 |  | 4.1176 |  | 9.8635 |  | 10.8185
02/03 17:00:00 | 23.8434 | 25.8881 | 24.9352 | 24.9377 | 24.814 | 25.3126 | 22.6935 | 36.6159 | 26.8585 | 31.6546 | 32.1088 | 31.0448 | 30.97 | 52.0975 | [14 empty] | 1.3222 |  | 239.6788 |  |  |  | 637.0074 |  | 417.9103 |  | 399.5485 |  | 443.2181 |  | 446.3702
02/03 18:00:00 | 23.7514 | 25.7994 | 24.841 | 24.7566 | 24.6369 | 25.1478 | 22.7205 | 33.8512 | 25.8211 | 29.1778 | 29.9277 | 28.9588 | 28.8169 | 61.8141 | [14 empty] | 1.0628 |  | 781.9237 |  |  |  | 1295.4945 |  | 1065.127 |  | 1016.7433 |  | 1079.4685 |  | 1088.8137
02/03 19:00:00 | 23.5615 | 25.5947 | 24.6236 | 24.3944 | 24.2882 | 24.8104 | 22.7801 | 33.474 | 24.9336 | 28.5743 | 29.621 | 28.7201 | 28.5782 | 42.9706 | [14 empty] | 0.61063 |  | 90.187 |  |  |  | 325.3361 |  | 207.2541 |  | 178.2127 |  | 203.0788 |  | 207.1435
02/03 20:00:00 | 23.0712 | 25.1079 | 24.1115 | 23.7084 | 23.6176 | 24.1378 | 22.8211 | 31.4403 | 23.9834 | 27.1752 | 27.8867 | 26.9951 | 26.8917 | 38.4031 | [14 empty] | 0.062569 |  | 48.4801 |  |  |  | 207.9263 |  | 126.0641 |  | 110.5932 |  | 130.1427 |  | 132.5118
02/03 21:00:00 | 22.4618 | 24.5223 | 23.5255 | 23.0641 | 22.8606 | 23.3834 | 22.2895 | 24.5672 | 17.8115 | 20.6144 | 21.59 | 20.922 | 20.9287 | 12.2191 | [14 empty] | 0.029696 |  | 152.4755 |  |  |  | 31.2744 |  | 70.4804 |  | 87.8131 |  | 75.7393 |  | 75.8562
02/03 22:00:00 | 22.0192 | 23.9621 | 23.0918 | 22.4904 | 22.182 | 22.8142 | 21.4487 | 24.015 | 17.3783 | 20.0904 | 21.1917 | 20.5803 | 20.5429 | 27.2726 | [14 empty] | 0.32549 |  | 10.6115 |  |  |  | 97.8967 |  | 51.584 |  | 36.9765 |  | 44.7861 |  | 45.2887
02/03 23:00:00 | 21.6343 | 23.3654 | 22.7018 | 21.9015 | 21.5169 | 22.1799 | 20.9732 | 22.7256 | 16.8895 | 19.2629 | 20.0802 | 19.5445 | 19.5088 | 29.6046 | [14 empty] | 0.43704 |  | 47.32 |  |  |  | 161.6724 |  | 106.9495 |  | 90.7135 |  | 101.2047 |  | 101.9237
02/03 24:00:00 | 21.2237 | 22.7126 | 22.2838 | 21.2552 | 20.815 | 21.5672 | 20.6412 | 21.8886 | 16.4446 | 18.6112 | 19.5124 | 19.0132 | 18.9467 | 31.1052 | [14 empty] | 0.33931 |  | 84.9456 |  |  |  | 214.9332 |  | 156.1013 |  | 134.3926 |  | 146.2161 |  | 147.8293
02/04 01:00:00 | 20.8268 | 22.2071 | 21.8793 | 20.7607 | 20.2782 | 21.0021 | 20.385 | 21.13 | 16.0139 | 18.0448 | 18.9151 | 41.22 | 18.4046 | 34.3101 | [14 empty] | 0.19516 |  | 173.7143 |  |  |  | 334.7485 |  | 264.5594 |  | 237.0036 |  | 47.747 |  | 252.982
02/04 02:00:00 | 20.461 | 21.7253 | 21.5064 | 20.2692 | 19.9456 | 20.5431 | 20.1646 | 33.3106 | 15.5406 | 17.3186 | 38.1075 | 48.3546 | 17.5257 | 35.7301 | [14 empty] | 0.087878 |  | 5.8537 |  |  |  | 407.6138 |  | 338.983 |  | 5.6523 |  | 159.3793 |  | 331.3982
02/04 03:00:00 | 20.235 | 21.2468 | 21.1319 | 19.9715 | 20.1498 | 20.088 | 19.9891 | 35.214 | 14.9728 | 16.4626 | 46.5895 | 47.0255 | 37.7804 | 37.8554 | [14 empty] | 0.060472 |  | 6.9774 |  |  |  | 523.6134 |  | 457.6543 |  | 76.2843 |  | 84.0898 |  | 0.0056366
02/04 04:00:00 | 20.2104 | 20.8613 | 20.753 | 20.1468 | 20.4357 | 19.8242 | 19.8609 | 47.2675 | 14.6944 | 16.3281 | 47.3956 | 47.7633 | 48.3442 | 39.185 | [14 empty] | 0.12219 |  | 65.3266 |  |  |  | 599.7888 |  | 522.4374 |  | 67.4135 |  | 73.5881 |  | 83.8912
02/04 05:00:00 | 20.3781 | 20.437 | 20.3619 | 20.3738 | 20.646 | 20.0117 | 19.7677 | 46.0572 | 29.5629 | 30.0411 | 46.5552 | 41.8894 | 46.6989 | 37.6781 | [14 empty] | 0.37254 |  | 70.2082 |  |  |  | 65.8569 |  | 58.3242 |  | 78.8016 |  | 17.7349 |  | 81.3747
02/04 06:00:00 | 20.5795 | 20.1414 | 20.1237 | 20.5514 | 20.723 | 20.2727 | 19.6993 | 39.409 | 39.8984 | 41.1168 | 41.9939 | 38.3306 | 46.5087 | 40.0856 | [14 empty] | 0.77459 |  | 0.45779 |  |  |  | 0.035054 |  | 1.0634 |  | 3.6416 |  | 3.0801 |  | 41.2562
02/04 07:00:00 | 20.6127 | 20.2076 | 20.2566 | 20.6503 | 20.6406 | 20.478 | 19.6333 | 35.9366 | 39.5878 | 42.1391 | 38.6976 | 36.8357 | 46.512 | 40.2015 | [14 empty] | 0.95923 |  | 18.1897 |  |  |  | 0.37673 |  | 3.754 |  | 2.2619 |  | 11.3288 |  | 39.8222
02/04 08:00:00 | 20.5754 | 20.3695 | 20.4829 | 20.594 | 20.4629 | 20.6256 | 19.5767 | 33.0365 | 39.2706 | 42.2706 | 36.7966 | 42.4121 | 42.2486 | 39.2196 | [14 empty] | 0.99742 |  | 38.2301 |  |  |  | 0.0026076 |  | 9.3091 |  | 5.8709 |  | 10.1923 |  | 9.1748
02/04 09:00:00 | 20.4974 | 20.5397 | 20.6979 | 20.4488 | 20.2917 | 20.7042 | 20.1874 | 40.4469 | 54.8866 | 55.3638 | 59.4989 | 65.9258 | 61.8445 | 79.6644 | [14 empty] | 0.096098 |  | 1538.013 |  |  |  | 613.9382 |  | 590.5185 |  | 406.6458 |  | 188.7482 |  | 317.55
02/04 10:00:00 | 20.39 | 21.3061 | 21.0232 | 20.5516 | 20.7883 | 21.154 | 21.759 | 50.8853 | 50.3284 | 53.1499 | 58.3374 | 59.1502 | 58.1708 | 66.7151 | [14 empty] | 1.8743 |  | 250.5822 |  |  |  | 268.5234 |  | 184.0161 |  | 70.1862 |  | 57.2289 |  | 73.006
02/04 11:00:00 | 20.5439 | 22.7303 | 22.0768 | 21.4905 | 21.7757 | 22.2416 | 22.9647 | 52.3868 | 42.5227 | 47.2089 | 56.559 | 52.0082 | 50.7393 | 17.6796 | [14 empty] | 5.8607 |  | 1204.5847 |  |  |  | 617.1783 |  | 871.9767 |  | 1511.6035 |  | 1178.4507 |  | 1092.9411
02/04 12:00:00 | 21.142 | 23.8668 | 23.091 | 22.6159 | 22.7726 | 23.3529 | 22.877 | 51.6029 | 37.9727 | 42.2149 | 48.812 | 45.0593 | 44.2067 | 11.8758 | [14 empty] | 3.0103 |  | 1578.2425 |  |  |  | 681.0495 |  | 920.4596 |  | 1364.2805 |  | 1101.145 |  | 1045.286
02/04 13:00:00 | 21.8482 | 24.4098 | 23.6282 | 23.4703 | 23.397 | 23.9879 | 22.7933 | 45.1192 | 35.0531 | 38.3634 | 42.8803 | 40.1733 | 39.6007 | 39.2112 | [14 empty] | 0.8932 |  | 34.9041 |  |  |  | 17.29 |  | 0.71876 |  | 13.4623 |  | 0.92566 |  | 0.15176
02/04 14:00:00 | 22.3183 | 24.6838 | 23.7984 | 23.8455 | 23.6737 | 24.265 | 23.0157 | 41.8904 | 32.4517 | 35.7663 | 39.8607 | 37.4121 | 36.7949 | 25.3348 | [14 empty] | 0.4864 |  | 274.09 |  |  |  | 50.6509 |  | 108.8172 |  | 211.0013 |  | 145.8618 |  | 131.3336
02/04 15:00:00 | 22.5313 | 24.891 | 23.928 | 24.0328 | 23.8559 | 24.4715 | 23.1352 | 39.3483 | 29.9 | 32.8831 | 36.2928 | 34.1501 | 33.4738 | 23.4386 | [14 empty] | 0.36468 |  | 253.1187 |  |  |  | 41.7501 |  | 89.2002 |  | 165.2321 |  | 114.7374 |  | 100.7053
02/04 16:00:00 | 22.6789 | 25.0826 | 24.0632 | 24.1861 | 24.007 | 24.6438 | 22.9726 | 39.8178 | 28.0552 | 31.386 | 34.9893 | 32.9688 | 32.3173 | 28.7462 | [14 empty] | 0.086232 |  | 122.5788 |  |  |  | 0.47757 |  | 6.9682 |  | 38.9763 |  | 17.8302 |  | 12.7526
02/04 17:00:00 | 22.7845 | 25.2248 | 24.1705 | 24.2861 | 24.1039 | 24.7598 | 22.7439 | 37.3258 | 27.2503 | 29.6821 | 32.775 | 30.9083 | 30.7039 | 31.4545 | [14 empty] | 0.0016472 |  | 34.4725 |  |  |  | 17.6754 |  | 3.1415 |  | 1.7436 |  | 0.29841 |  | 0.56343
02/04 18:00:00 | 22.8626 | 25.2317 | 24.1725 | 24.2617 | 24.0817 | 24.7553 | 22.8142 | 33.2789 | 25.4642 | 27.1225 | 29.2416 | 27.5424 | 27.3009 | 40.5676 | [14 empty] | 0.0023467 |  | 53.1243 |  |  |  | 228.1126 |  | 180.7696 |  | 128.2771 |  | 169.6549 |  | 176.004
02/04 19:00:00 | 22.8687 | 25.1628 | 24.1005 | 24.1483 | 23.9723 | 24.6564 | 22.6854 | 32.9958 | 24.9991 | 26.7679 | 28.9563 | 27.3939 | 27.2777 | 49.8991 | [14 empty] | 0.03361 |  | 285.7186 |  |  |  | 620.0077 |  | 535.0485 |  | 438.5973 |  | 506.4826 |  | 511.727
02/04 20:00:00 | 22.7224 | 24.9611 | 23.917 | 23.8689 | 23.6891 | 24.4052 | 22.524 | 26.3648 | 18.6799 | 20.6762 | 22.6633 | 21.4607 | 21.4433 | 5.0799 | [14 empty] | 0.039361 |  | 453.0451 |  |  |  | 184.9592 |  | 243.2449 |  | 309.1747 |  | 268.3285 |  | 267.759
02/04 21:00:00 | 22.5237 | 24.6027 | 23.6424 | 23.4388 | 23.2152 | 23.9945 | 21.8571 | 24.1874 | 18.0227 | 19.3866 | 20.8376 | 19.8082 | 19.7383 | 24.6553 | [14 empty] | 0.44439 |  | 0.21892 |  |  |  | 43.9915 |  | 27.7597 |  | 14.5752 |  | 23.4949 |  | 24.1769
02/04 22:00:00 | 22.3166 | 24.1368 | 23.334 | 22.9705 | 22.6617 | 23.4923 | 21.4355 | 22.9943 | 17.3439 | 18.5283 | 19.9023 | 18.9256 | 18.8621 | 25.1561 | [14 empty] | 0.77634 |  | 4.6733 |  |  |  | 61.0307 |  | 43.9274 |  | 27.6023 |  | 38.8191 |  | 39.6141
02/04 23:00:00 | 22.0862 | 23.6576 | 23.0123 | 22.4878 | 22.1157 | 22.9812 | 21.1961 | 22.0369 | 16.8173 | 17.8223 | 19.2079 | 18.2771 | 18.2039 | 27.9312 | [14 empty] | 0.79225 |  | 34.7428 |  |  |  | 123.5193 |  | 102.1889 |  | 76.0968 |  | 93.2023 |  | 94.6197
02/04 24:00:00 | 21.8379 | 23.2477 | 22.7509 | 22.0741 | 21.6488 | 22.5492 | 21.0195 | 21.1711 | 16.28 | 17.1918 | 18.5593 | 17.6927 | 17.5825 | 27.5751 | [14 empty] | 0.66978 |  | 41.0112 |  |  |  | 127.5803 |  | 107.8144 |  | 81.2852 |  | 97.6626 |  | 99.8525
02/05 01:00:00 | 21.5725 | 22.8281 | 22.4878 | 21.7082 | 21.2228 | 22.1072 | 20.922 | 20.8633 | 15.9651 | 16.9133 | 18.3893 | 17.5844 | 17.5063 | 28.4762 | [14 empty] | 0.42311 |  | 57.9562 |  |  |  | 156.5289 |  | 133.6996 |  | 101.7466 |  | 118.6324 |  | 120.3378
02/05 02:00:00 | 21.2884 | 22.4608 | 22.2044 | 21.3233 | 20.7678 | 21.7257 | 20.8528 | 20.5482 | 15.7028 | 16.6979 | 18.2524 | 17.491 | 17.4001 | 29.7066 | [14 empty] | 0.18972 |  | 83.8761 |  |  |  | 196.1076 |  | 169.2261 |  | 131.1985 |  | 149.2216 |  | 151.4504
02/05 03:00:00 | 20.9786 | 22.0821 | 21.8974 | 20.9138 | 20.2916 | 21.3172 | 20.8199 | 20.2364 | 15.3871 | 16.4295 | 18.0249 | 34.3039 | 17.2308 | 28.1238 | [14 empty] | 0.025164 |  | 62.2106 |  |  |  | 162.2234 |  | 136.7576 |  | 101.9886 |  | 38.1933 |  | 118.6589
02/05 04:00:00 | 20.6747 | 21.7729 | 21.5927 | 20.5842 | 20.0867 | 20.9847 | 20.7537 | 19.1786 | 14.9091 | 13.1588 | 17.1345 | 44.7873 | 16.3686 | 29.004 | [14 empty] | 0.0062345 |  | 96.5382 |  |  |  | 198.6676 |  | 251.07 |  | 140.8847 |  | 249.1124 |  | 159.6542
02/05 05:00:00 | 20.3991 | 21.5086 | 21.3555 | 20.2968 | 20.2944 | 20.6955 | 20.7426 | 14.6309 | 14.2358 | 12.6153 | 31.7731 | 43.5191 | 15.162 | 29.3861 | [14 empty] | 0.118 |  | 217.7155 |  |  |  | 229.5311 |  | 281.2597 |  | 5.6976 |  | 199.743 |  | 202.3253
02/05 06:00:00 | 20.1853 | 21.2659 | 21.1997 | 20.1854 | 20.6165 | 20.4346 | 20.7718 | 22.5409 | 13.689 | 12.3365 | 43.0101 | 37.5983 | 31.9338 | 28.6968 | [14 empty] | 0.34387 |  | 37.895 |  |  |  | 225.233 |  | 267.6587 |  | 204.8702 |  | 79.2373 |  | 10.478
02/05 07:00:00 | 20.1186 | 21.0227 | 21.0377 | 20.4156 | 20.8915 | 20.3256 | 20.8014 | 41.4959 | 11.4857 | 12.2027 | 43.7427 | 30.3137 | 43.9862 | 27.9598 | [14 empty] | 0.46628 |  | 183.2265 |  |  |  | 271.3955 |  | 248.287 |  | 249.098 |  | 5.5407 |  | 256.8441
02/05 08:00:00 | 20.3504 | 20.8291 | 20.8804 | 20.7465 | 20.9661 | 20.5726 | 20.7853 | 42.6814 | 11.4037 | 11.7814 | 38.1716 | 29.8958 | 35.1298 | 28.7343 | [14 empty] | 0.18918 |  | 194.5213 |  |  |  | 300.3514 |  | 287.4028 |  | 89.061 |  | 1.3489 |  | 40.9014
02/05 09:00:00 | 20.703 | 20.6965 | 20.7319 | 21.0525 | 20.9711 | 20.8768 | 21.0988 | 49.8866 | 14.8379 | 14.038 | 54.2099 | 56.7121 | 53.441 | 73.4507 | [14 empty] | 0.15661 |  | 555.2667 |  |  |  | 3435.4562 |  | 3529.8654 |  | 370.2087 |  | 280.1791 |  | 400.3882
02/05 10:00:00 | 21.0845 | 20.5725 | 20.5936 | 21.7249 | 21.619 | 21.6628 | 22.1183 | 49.6321 | 27.5254 | 25.1448 | 46.0264 | 55.5283 | 54.3002 | 58.32 | [14 empty] | 1.0688 |  | 75.478 |  |  |  | 948.3048 |  | 1100.591 |  | 151.1306 |  | 7.7932 |  | 16.1587
02/05 11:00:00 | 21.4481 | 20.544 | 20.5604 | 22.7515 | 22.5432 | 22.795 | 22.9054 | 51.0893 | 53.9744 | 49.0423 | 41.8663 | 46.6771 | 46.1106 | 29.4667 | [14 empty] | 2.1236 |  | 467.5336 |  |  |  | 600.623 |  | 383.203 |  | 153.7481 |  | 296.1952 |  | 277.0168
02/05 12:00:00 | 21.7882 | 21.213 | 20.9031 | 23.1514 | 23.2281 | 23.6023 | 22.82 | 47.2014 | 50.4751 | 51.2153 | 39.3895 | 41.9706 | 41.875 | 21.0637 | [14 empty] | 1.0644 |  | 683.1801 |  |  |  | 865.032 |  | 909.1175 |  | 335.8349 |  | 437.1001 |  | 433.1111
02/05 13:00:00 | 22.0879 | 22.6158 | 21.6644 | 23.2108 | 23.5148 | 23.8544 | 22.9446 | 42.9857 | 40.1805 | 50.512 | 36.5422 | 39.2339 | 38.9862 | 28.4204 | [14 empty] | 0.7339 |  | 212.1493 |  |  |  | 138.3007 |  | 488.0377 |  | 65.9639 |  | 116.9328 |  | 111.6367
02/05 14:00:00 | 22.2562 | 23.7516 | 22.6813 | 23.2248 | 23.5974 | 23.9521 | 23.2211 | 39.7747 | 34.4088 | 42.5879 | 33.1756 | 35.6472 | 35.2565 | 14.1606 | [14 empty] | 0.93099 |  | 656.0821 |  |  |  | 409.9896 |  | 808.1142 |  | 361.5709 |  | 461.6723 |  | 445.0368
02/05 15:00:00 | 22.6528 | 24.4598 | 23.8708 | 23.3698 | 23.8486 | 24.2901 | 23.0848 | 36.2374 | 31.7595 | 38.1288 | 29.9087 | 32.1913 | 31.7991 | 16.6814 | [14 empty] | 0.18659 |  | 382.4365 |  |  |  | 227.3504 |  | 459.9944 |  | 174.9618 |  | 240.5568 |  | 228.5457
02/05 16:00:00 | 22.9846 | 24.925 | 24.4796 | 23.554 | 24.124 | 24.6182 | 22.8858 | 33.6195 | 29.829 | 35.6594 | 27.7489 | 29.8471 | 29.4773 | 17.6906 | [14 empty] | 0.0097497 |  | 253.7282 |  |  |  | 147.3415 |  | 322.8756 |  | 101.17 |  | 147.7803 |  | 138.9266
02/05 17:00:00 | 23.1033 | 25.1443 | 24.6849 | 23.645 | 24.2551 | 24.7635 | 22.6775 | 33.7118 | 28.854 | 34.8222 | 27.8696 | 29.8316 | 29.4654 | 18.7678 | [14 empty] | 0.18136 |  | 223.3218 |  |  |  | 101.73 |  | 257.7426 |  | 82.8412 |  | 122.4059 |  | 114.4378
02/05 18:00:00 | 23.1331 | 25.2189 | 24.7638 | 23.646 | 24.2788 | 24.7955 | 22.5902 | 27.0483 | 27.6985 | 33.0624 | 26.308 | 28.1111 | 27.8106 | 43.3844 | [14 empty] | 0.29472 |  | 266.8667 |  |  |  | 246.0459 |  | 106.5426 |  | 291.6033 |  | 233.2714 |  | 242.5432
02/05 19:00:00 | 23.081 | 25.2417 | 24.7929 | 23.5828 | 24.239 | 24.7545 | 22.8812 | 25.7304 | 26.1096 | 31.0006 | 24.703 | 26.2915 | 26.0551 | 8.2802 | [14 empty] | 0.039922 |  | 304.5094 |  |  |  | 317.8852 |  | 516.214 |  | 269.7072 |  | 324.4067 |  | 315.9473
02/05 20:00:00 | 23.0106 | 25.1987 | 24.7701 | 23.4485 | 24.1203 | 24.6286 | 22.6022 | 19.7347 | 18.8804 | 23.0747 | 18.7009 | 19.7522 | 19.6665 | 12.0977 | [14 empty] | 0.16674 |  | 58.324 |  |  |  | 46.0063 |  | 120.4964 |  | 43.6032 |  | 58.5928 |  | 57.2875
02/05 21:00:00 | 22.9305 | 25.0743 | 24.705 | 23.2673 | 23.9106 | 24.4194 | 22.3375 | 19.1264 | 18.2153 | 22.0795 | 17.9763 | 18.9663 | 18.9272 | 16.8297 | [14 empty] | 0.35165 |  | 5.2749 |  |  |  | 1.9199 |  | 27.5607 |  | 1.3148 |  | 4.5654 |  | 4.3998
02/05 22:00:00 | 22.8386 | 24.8618 | 24.6069 | 23.0509 | 23.5877 | 24.1305 | 22.1335 | 18.0917 | 17.4993 | 20.9359 | 16.9655 | 17.9895 | 17.8735 | 18.684 | [14 empty] | 0.49712 |  | 0.35076 |  |  |  | 1.4035 |  | 5.0713 |  | 2.9531 |  | 0.48224 |  | 0.6569
02/05 23:00:00 | 22.7322 | 24.5988 | 24.4756 | 22.8483 | 23.2498 | 23.8102 | 21.9204 | 17.531 | 16.8997 | 20.0553 | 16.3484 | 17.3319 | 17.243 | 19.4804 | [14 empty] | 0.65893 |  | 3.7999 |  |  |  | 6.6602 |  | 0.33051 |  | 9.809 |  | 4.6158 |  | 5.006
02/05 24:00:00 | 22.6089 | 24.3469 | 24.3078 | 22.6316 | 22.8876 | 23.5237 | 21.7435 | 20.5873 | 16.3352 | 19.2604 | 15.7271 | 16.7132 | 16.5917 | 21.4013 | [14 empty] | 0.74896 |  | 0.66254 |  |  |  | 25.6647 |  | 4.5833 |  | 32.1965 |  | 21.9775 |  | 23.132
02/06 01:00:00 | 22.4462 | 24.0581 | 24.0944 | 22.369 | 22.5442 | 23.1939 | 21.613 | 19.4817 | 15.8318 | 18.6056 | 15.2906 | 16.2422 | 16.1185 | 21.802 | [14 empty] | 0.69423 |  | 5.3838 |  |  |  | 35.643 |  | 10.2169 |  | 42.3976 |  | 30.9118 |  | 32.3024
02/06 02:00:00 | 22.2265 | 23.8204 | 23.8785 | 22.1021 | 22.2032 | 22.9243 | 21.4518 | 14.7718 | 15.1801 | 17.5286 | 14.1839 | 15.0899 | 14.9516 | 23.4107 | [14 empty] | 0.60011 |  | 74.6304 |  |  |  | 67.7426 |  | 34.5994 |  | 85.1341 |  | 69.2357 |  | 71.5568
02/06 03:00:00 | 22.0266 | 23.599 | 23.6568 | 21.8311 | 21.932 | 22.668 | 21.354 | 13.7495 | 14.434 | 13.4271 | 13.0954 | 14.0023 | 13.8502 | 22.9811 | [14 empty] | 0.45246 |  | 85.2226 |  |  |  | 73.0521 |  | 91.2779 |  | 97.7259 |  | 80.6185 |  | 83.3722
02/06 04:00:00 | 21.8749 | 23.3777 | 23.4642 | 21.5663 | 21.6799 | 22.4144 | 21.2337 | 18.1473 | 14.227 | 17.2295 | 13.9199 | 14.7679 | 14.6181 | 25.2481 | [14 empty] | 0.41118 |  | 50.4221 |  |  |  | 121.4667 |  | 64.2986 |  | 128.3297 |  | 109.8357 |  | 112.9975
02/06 05:00:00 | 21.6782 | 23.1269 | 23.2664 | 21.2762 | 21.39 | 22.1241 | 21.0922 | 14.3979 | 13.9839 | 16.3759 | 13.5791 | 14.3728 | 14.2835 | 27.1302 | [14 empty] | 0.3434 |  | 162.1115 |  |  |  | 172.826 |  | 115.6559 |  | 183.6315 |  | 162.7518 |  | 165.0371
02/06 06:00:00 | 21.4453 | 22.8584 | 22.9905 | 20.9766 | 21.0788 | 21.8198 | 20.9868 | 14.7371 | 13.7375 | 16.1458 | 13.6804 | 14.4598 | 14.3579 | 26.5344 | [14 empty] | 0.21026 |  | 139.1769 |  |  |  | 163.7606 |  | 107.9233 |  | 165.2261 |  | 145.796 |  | 148.2668
02/06 07:00:00 | 21.2646 | 22.58 | 22.7115 | 20.6721 | 20.7559 | 21.5054 | 20.9383 | 14.9507 | 13.5326 | 15.9814 | 13.7856 | 14.5521 | 14.4347 | 26.9337 | [14 empty] | 0.10647 |  | 143.5929 |  |  |  | 179.5883 |  | 119.9525 |  | 172.8728 |  | 153.3026 |  | 156.2233
02/06 08:00:00 | 21.0787 | 22.2958 | 22.431 | 20.3665 | 20.4278 | 21.1852 | 21.2013 | 18.347 | 17.9505 | 20.066 | 41.1703 | 44.7359 | 42.7615 | 74.8326 | [14 empty] | 0.015033 |  | 3190.62 |  |  |  | 3235.5727 |  | 2999.3753 |  | 1133.1477 |  | 905.8113 |  | 1028.5547
02/06 09:00:00 | 20.9022 | 22.0328 | 22.1759 | 20.255 | 20.316 | 21.0682 | 22.5253 | 39.4012 | 30.9446 | 30.2293 | 59.1629 | 61.7207 | 59.8014 | 47.7047 | [14 empty] | 2.6345 |  | 68.9474 |  |  |  | 280.9012 |  | 305.3879 |  | 131.29 |  | 196.448 |  | 146.3298
02/06 10:00:00 | 21.0355 | 22.0312 | 22.189 | 21.2791 | 21.6101 | 22.1718 | 23.4596 | 46.9672 | 38.0909 | 36.2909 | 52.1602 | 52.2438 | 41.699 | 4.8898 | [14 empty] | 5.8762 |  | 1770.5074 |  |  |  | 1102.3102 |  | 986.0296 |  | 2234.4865 |  | 2242.3983 |  | 1354.9164
02/06 11:00:00 | 21.9848 | 23.333 | 23.0668 | 23.4838 | 24.0153 | 24.4276 | 23.5514 | 38.8449 | 26.2779 | 28.3249 | 40.5732 | 38.9039 | 33.6031 | 3.3502 | [14 empty] | 2.4541 |  | 1259.8712 |  |  |  | 525.6776 |  | 623.734 |  | 1385.551 |  | 1264.0664 |  | 915.2354
02/06 12:00:00 | 23.7909 | 25.3422 | 24.6315 | 25.3606 | 25.5661 | 25.8309 | 23.626 | 33.2539 | 22.0833 | 24.3778 | 34.1315 | 32.6991 | 29.2532 | 3.1212 | [14 empty] | 0.027187 |  | 907.9772 |  |  |  | 359.5606 |  | 451.842 |  | 961.6379 |  | 874.8497 |  | 682.8829
02/06 13:00:00 | 24.8033 | 26.3389 | 25.5102 | 26.1075 | 26.2216 | 26.4362 | 23.6507 | 30.5515 | 20.7484 | 22.6785 | 32.3502 | 31.6117 | 27.646 | 2.8333 | [14 empty] | 1.3286 |  | 768.2971 |  |  |  | 320.9522 |  | 393.8312 |  | 871.2504 |  | 828.1979 |  | 615.6698
02/06 14:00:00 | 24.9584 | 26.4338 | 25.5657 | 26.153 | 26.2744 | 26.5015 | 23.6617 | 28.2675 | 18.2905 | 20.8999 | 28.7439 | 27.293 | 23.789 | 2.7232 | [14 empty] | 1.6814 |  | 652.5136 |  |  |  | 242.3405 |  | 330.3933 |  | 677.08 |  | 603.6763 |  | 443.7692
02/06 15:00:00 | 25.136 | 26.655 | 25.7962 | 26.3534 | 26.4996 | 26.7271 | 23.765 | 25.4245 | 15.3658 | 18.602 | 23.6409 | 21.8125 | 19.581 | 2.6186 | [14 empty] | 1.8797 |  | 520.11 |  |  |  | 162.4925 |  | 255.471 |  | 441.9372 |  | 368.4057 |  | 287.7258
02/06 16:00:00 | 25.6808 | 27.2593 | 26.3906 | 26.9265 | 27.0742 | 27.2619 | 23.8646 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5411 | [14 empty] | 3.2983 |  | 6.4572 |  |  |  | 6.4572 |  | 6.4572 |  | 6.4572 |  | 6.4572 |  | 6.4572
02/06 17:00:00 | 25.7532 | 27.5855 | 26.6037 | 27.0487 | 27.2144 | 27.4623 | 23.9163 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5827 | [14 empty] | 3.3745 |  | 6.6702 |  |  |  | 6.6702 |  | 6.6702 |  | 6.6702 |  | 6.6702 |  | 6.6702
02/06 18:00:00 | 25.5238 | 27.6196 | 26.5347 | 26.8645 | 27.0485 | 27.4057 | 23.638 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6131 | [14 empty] | 3.5562 |  | 6.8284 |  |  |  | 6.8284 |  | 6.8284 |  | 6.8284 |  | 6.8284 |  | 6.8284
02/06 19:00:00 | 25.2565 | 27.4998 | 26.3433 | 26.574 | 26.7436 | 27.1881 | 23.1691 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8322 | [14 empty] | 4.3572 |  | 14.6857 |  |  |  | 14.6857 |  | 14.6857 |  | 14.6857 |  | 14.6857 |  | 14.6857
02/06 20:00:00 | 24.6524 | 26.8788 | 25.721 | 25.9003 | 26.0572 | 26.4762 | 22.7759 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7804 | [14 empty] | 3.5213 |  | 14.2911 |  |  |  | 14.2911 |  | 14.2911 |  | 14.2911 |  | 14.2911 |  | 14.2911
02/06 21:00:00 | 24.0811 | 26.2867 | 25.1522 | 25.2505 | 25.3849 | 25.865 | 22.4651 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7969 | [14 empty] | 2.6114 |  | 14.4166 |  |  |  | 14.4166 |  | 14.4166 |  | 14.4166 |  | 14.4166 |  | 14.4166
02/06 22:00:00 | 23.6801 | 25.8311 | 24.6957 | 24.7588 | 24.8718 | 25.3932 | 22.1764 | 28.1965 | 23.5815 | 22.7728 | 34.609 | 36.9749 | 31.5277 | 3.8215 | [14 empty] | 2.2611 |  | 594.1375 |  |  |  | 390.456 |  | 359.1507 |  | 947.8659 |  | 1099.1462 |  | 767.6335
02/06 23:00:00 | 23.7836 | 25.6787 | 24.6364 | 24.8198 | 24.9026 | 25.368 | 21.9235 | 21.707 | 14.744 | 15.9848 | 23.176 | 23.4249 | 20.4924 | 3.8618 | [14 empty] | 3.46 |  | 318.4515 |  |  |  | 118.423 |  | 146.9672 |  | 373.0396 |  | 382.7168 |  | 276.5784
02/06 24:00:00 | 23.8688 | 25.5884 | 24.64 | 24.9517 | 25.0058 | 25.4001 | 21.6021 | 20.8279 | 13.6413 | 15.1824 | 21.863 | 21.8787 | 19.3102 | 3.8445 | [14 empty] | 5.1377 |  | 288.4346 |  |  |  | 95.9761 |  | 128.5478 |  | 324.6647 |  | 325.2303 |  | 239.1874
02/07 01:00:00 | 23.8701 | 25.4786 | 24.5791 | 24.9494 | 24.9772 | 25.3386 | 21.2468 | 20.0141 | 13.1558 | 14.6832 | 21.0251 | 21.0512 | 18.5983 | 4.0054 | [14 empty] | 6.8821 |  | 256.2793 |  |  |  | 83.7302 |  | 114.0155 |  | 289.6706 |  | 290.5612 |  | 212.9544
02/07 02:00:00 | 23.8409 | 25.364 | 24.5 | 24.8967 | 24.8954 | 25.2278 | 21.0486 | 19.743 | 12.8654 | 14.4562 | 20.7429 | 20.7866 | 18.4362 | 3.8987 | [14 empty] | 7.797 |  | 251.0396 |  |  |  | 80.4005 |  | 111.4594 |  | 283.7263 |  | 285.2006 |  | 211.3381
02/07 03:00:00 | 23.7631 | 25.2208 | 24.3818 | 24.7876 | 24.7651 | 25.0754 | 20.9242 | 15.3603 | 12.4284 | 13.75 | 19.409 | 19.4734 | 17.2853 | 3.9677 | [14 empty] | 8.0593 |  | 129.7925 |  |  |  | 71.5832 |  | 95.6928 |  | 238.4343 |  | 240.4279 |  | 177.3593
02/07 04:00:00 | 23.6599 | 25.0656 | 24.2495 | 24.6507 | 24.6069 | 24.9091 | 20.8482 | 15.3953 | 12.0013 | 11.1991 | 18.919 | 18.9864 | 16.8997 | 4.0074 | [14 empty] | 7.9054 |  | 129.6834 |  |  |  | 63.9011 |  | 51.7195 |  | 222.3543 |  | 224.3707 |  | 166.2112
02/07 05:00:00 | 23.5779 | 24.9026 | 24.1305 | 24.5055 | 24.4417 | 24.7396 | 20.663 | 14.2767 | 9.9497 | 10.792 | 15.3967 | 15.7641 | 13.9332 | 3.9843 | [14 empty] | 8.497 |  | 105.9329 |  |  |  | 35.5855 |  | 46.344 |  | 130.2416 |  | 138.7618 |  | 98.9794
02/07 06:00:00 | 23.5016 | 24.785 | 24.0495 | 24.3849 | 24.3096 | 24.6078 | 20.5089 | 13.9938 | 9.7759 | 10.5003 | 15.2428 | 15.5277 | 13.7755 | 4.1481 | [14 empty] | 8.9563 |  | 96.9383 |  |  |  | 31.6725 |  | 40.3509 |  | 123.0921 |  | 129.4958 |  | 92.6878
02/07 07:00:00 | 23.4396 | 24.7027 | 23.9857 | 24.3107 | 24.2277 | 24.5261 | 20.476 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1147 | [14 empty] | 8.7829 |  | 16.9304 |  |  |  | 16.9304 |  | 16.9304 |  | 16.9304 |  | 16.9304 |  | 16.9304
02/07 08:00:00 | 23.1795 | 24.5195 | 23.7822 | 24.0449 | 23.9555 | 24.2809 | 20.4268 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0601 | [14 empty] | 7.5774 |  | 16.4842 |  |  |  | 16.4842 |  | 16.4842 |  | 16.4842 |  | 16.4842 |  | 16.4842
02/07 09:00:00 | 22.885 | 24.3364 | 23.5432 | 23.7207 | 23.6218 | 23.9781 | 20.4115 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1128 | [14 empty] | 6.1183 |  | 16.9153 |  |  |  | 16.9153 |  | 16.9153 |  | 16.9153 |  | 16.9153 |  | 16.9153
02/07 10:00:00 | 22.7441 | 24.2663 | 23.4464 | 23.5355 | 23.4226 | 23.8084 | 20.4288 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1838 | [14 empty] | 5.3603 |  | 17.5042 |  |  |  | 17.5042 |  | 17.5042 |  | 17.5042 |  | 17.5042 |  | 17.5042
02/07 11:00:00 | 22.8008 | 24.2988 | 23.5476 | 23.5426 | 23.4149 | 23.8266 | 20.5863 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2316 | [14 empty] | 4.904 |  | 17.906 |  |  |  | 17.906 |  | 17.906 |  | 17.906 |  | 17.906 |  | 17.906
02/07 12:00:00 | 22.9345 | 24.4071 | 23.7153 | 23.6096 | 23.4744 | 23.9033 | 20.8575 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1016 | [14 empty] | 4.3138 |  | 4.4166 |  |  |  | 4.4166 |  | 4.4166 |  | 4.4166 |  | 4.4166 |  | 4.4166
02/07 13:00:00 | 23.0378 | 24.4957 | 23.8397 | 23.6665 | 23.5237 | 23.9654 | 21.0478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.9602 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/07 14:00:00 | 22.9404 | 24.4132 | 23.7541 | 23.567 | 23.416 | 23.8782 | 21.3786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.4393 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/07 15:00:00 | 22.9593 | 24.4392 | 23.7922 | 23.5658 | 23.4052 | 23.9079 | 21.719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.5383 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/07 16:00:00 | 23.3128 | 24.8305 | 24.2385 | 23.8901 | 23.7253 | 24.319 | 21.968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.8084 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/07 17:00:00 | 23.6257 | 25.1689 | 24.6026 | 24.1791 | 24.0132 | 24.6495 | 22.189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.0639 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/07 18:00:00 | 23.7008 | 25.2415 | 24.6687 | 24.2387 | 24.071 | 24.6994 | 22.197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.2613 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/07 19:00:00 | 23.6415 | 25.1895 | 24.6111 | 24.1626 | 23.9918 | 24.614 | 22.0717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.4644 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/07 20:00:00 | 23.3616 | 24.871 | 24.341 | 23.8654 | 23.6204 | 24.2449 | 21.9382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.0261 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/07 21:00:00 | 23.0225 | 24.5068 | 23.9801 | 23.5044 | 23.2198 | 23.8441 | 21.7601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.5938 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/07 22:00:00 | 22.7781 | 24.1998 | 23.6492 | 23.1717 | 22.8894 | 23.5172 | 21.6114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.3611 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/07 23:00:00 | 22.6296 | 23.9885 | 23.4314 | 22.9503 | 22.6709 | 23.301 | 21.4286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.4423 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/07 24:00:00 | 22.441 | 23.8004 | 23.2507 | 22.7636 | 22.4839 | 23.1157 | 21.3183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.2605 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/08 01:00:00 | 22.1808 | 23.5359 | 23.0516 | 22.5568 | 22.2749 | 22.9087 | 21.2511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.86432 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/08 02:00:00 | 22.0242 | 23.3679 | 22.944 | 22.4413 | 22.1569 | 22.7918 | 21.1988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.68121 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/08 03:00:00 | 21.9252 | 23.2578 | 22.8363 | 22.3256 | 22.038 | 22.674 | 21.1861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.54622 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/08 04:00:00 | 21.8343 | 23.1543 | 22.7355 | 22.216 | 21.9251 | 22.5621 | 21.179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.42944 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/08 05:00:00 | 21.7366 | 23.0033 | 22.6288 | 22.0589 | 21.7624 | 22.4011 | 21.1012 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2451 | [14 empty] | 0.40367 |  | 39.0011 |  |  |  | 39.0011 |  | 39.0011 |  | 39.0011 |  | 39.0011 |  | 39.0011
02/08 06:00:00 | 21.5748 | 22.7845 | 22.4551 | 21.8286 | 21.5234 | 22.1654 | 21.0491 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3705 | [14 empty] | 0.2764 |  | 19.1014 |  |  |  | 19.1014 |  | 19.1014 |  | 19.1014 |  | 19.1014 |  | 19.1014
02/08 07:00:00 | 21.3606 | 22.5644 | 22.2754 | 21.5984 | 21.2839 | 21.9299 | 20.9527 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4518 | [14 empty] | 0.16642 |  | 19.8182 |  |  |  | 19.8182 |  | 19.8182 |  | 19.8182 |  | 19.8182 |  | 19.8182
02/08 08:00:00 | 21.1949 | 22.3427 | 22.1395 | 21.4181 | 21.0443 | 21.7457 | 20.8413 | 0 | 0 | 0 | 0 | 0 | 0 | 4.574 | [14 empty] | 0.12502 |  | 20.9214 |  |  |  | 20.9214 |  | 20.9214 |  | 20.9214 |  | 20.9214 |  | 20.9214
02/08 09:00:00 | 21.0478 | 22.1401 | 21.9702 | 21.2548 | 20.8276 | 21.5792 | 20.6633 | 24.3738 | 23.3138 | 21.0903 | 30.119 | 59.5614 | 28.302 | 4.3314 | [14 empty] | 0.14786 |  | 401.6959 |  |  |  | 360.3301 |  | 280.8579 |  | 664.9977 |  | 3050.3519 |  | 574.5864
02/08 10:00:00 | 21.3394 | 22.269 | 22.1182 | 21.5481 | 21.4185 | 21.7772 | 20.5598 | 21.2145 | 15.0594 | 15.2622 | 21.811 | 43.1456 | 19.1732 | 4.4004 | [14 empty] | 0.60782 |  | 282.7146 |  |  |  | 113.6143 |  | 117.9788 |  | 303.1293 |  | 1501.1876 |  | 218.2351
02/08 11:00:00 | 21.7698 | 22.5239 | 22.3773 | 21.9725 | 23.426 | 22.1479 | 20.64 | 28.2253 | 13.5775 | 14.0929 | 28.9543 | 32.3052 | 17.6529 | 4.5519 | [14 empty] | 1.2764 |  | 560.4296 |  |  |  | 81.4615 |  | 91.0316 |  | 595.4776 |  | 770.248 |  | 171.6369
02/08 12:00:00 | 22.185 | 22.7796 | 22.618 | 22.3582 | 24.6069 | 22.4546 | 20.759 | 25.7653 | 11.279 | 11.272 | 25.9685 | 29.4667 | 14.1952 | 5.7246 | [14 empty] | 2.0333 |  | 401.6285 |  |  |  | 30.8512 |  | 30.7734 |  | 409.814 |  | 563.6851 |  | 71.7507
02/08 13:00:00 | 22.5926 | 22.9434 | 22.758 | 22.9331 | 24.8417 | 22.6151 | 20.6965 | 22.9499 | 12.1988 | 12.7412 | 21.8921 | 28.1913 | 15.3874 | 11.7867 | [14 empty] | 3.5952 |  | 124.6168 |  |  |  | 0.16982 |  | 0.91113 |  | 102.1196 |  | 269.1108 |  | 12.9652
02/08 14:00:00 | 22.6303 | 22.8519 | 22.6118 | 23.0858 | 24.7242 | 22.4996 | 20.8917 | 18.7014 | 10.231 | 10.4539 | 18.7918 | 24.2509 | 13.2389 | 58.4803 | [14 empty] | 3.0227 |  | 1582.3603 |  |  |  | 2328.0021 |  | 2306.5374 |  | 1575.1808 |  | 1171.6516 |  | 2046.7851
02/08 15:00:00 | 22.6268 | 22.8245 | 22.5379 | 23.0677 | 24.6216 | 22.4417 | 22.0156 | 21.8045 | 11.1186 | 11.8533 | 20.7689 | 26.0312 | 14.226 | 49.1807 | [14 empty] | 0.37355 |  | 749.4522 |  |  |  | 1448.7234 |  | 1393.329 |  | 807.2255 |  | 535.8983 |  | 1221.8275
02/08 16:00:00 | 22.8505 | 23.0137 | 22.7222 | 23.2353 | 24.7465 | 22.6173 | 22.7008 | 17.3052 | 9.2307 | 9.5912 | 17.4132 | 21.827 | 12.081 | 2.3647 | [14 empty] | 0.022435 |  | 223.2195 |  |  |  | 47.1417 |  | 52.2225 |  | 226.4575 |  | 378.7836 |  | 94.4077
02/08 17:00:00 | 22.9934 | 23.1694 | 22.8515 | 23.342 | 24.8123 | 22.7457 | 22.161 | 19.185 | 9.8845 | 10.569 | 18.255 | 22.7529 | 12.4022 | 1.6934 | [14 empty] | 0.69303 |  | 305.9545 |  |  |  | 67.0929 |  | 78.7751 |  | 274.2847 |  | 443.5034 |  | 114.6782
02/08 18:00:00 | 22.9507 | 23.1216 | 22.7813 | 23.2692 | 24.7172 | 22.6737 | 21.4121 | 17.5256 | 9.25 | 9.7639 | 16.6104 | 20.6194 | 11.3107 | 0.86722 | [14 empty] | 2.3673 |  | 277.503 |  |  |  | 70.2713 |  | 79.1501 |  | 247.849 |  | 390.1471 |  | 109.0657
02/08 19:00:00 | 22.8064 | 22.9821 | 22.6064 | 23.0892 | 24.4655 | 22.501 | 20.6005 | 17.0157 | 9.0541 | 9.698 | 16.0235 | 19.7418 | 11.1368 | 0.57701 | [14 empty] | 4.8658 |  | 270.2297 |  |  |  | 71.8619 |  | 83.1927 |  | 238.5944 |  | 367.2883 |  | 111.5082
02/08 20:00:00 | 22.3881 | 22.5625 | 22.141 | 22.6369 | 23.9261 | 22.0447 | 19.826 | 16.9802 | 9.1617 | 9.812 | 15.9233 | 19.4776 | 11.3063 | 0.47779 | [14 empty] | 6.5647 |  | 272.3287 |  |  |  | 75.411 |  | 87.1271 |  | 238.5623 |  | 360.9912 |  | 117.2561
02/08 21:00:00 | 21.8342 | 21.9821 | 21.5305 | 22.0384 | 23.3083 | 21.4384 | 19.3384 | 13.5771 | 7.0141 | 7.8763 | 12.577 | 15.2243 | 9.2921 | 0.40372 | [14 empty] | 6.2289 |  | 173.5384 |  |  |  | 43.6965 |  | 55.8397 |  | 148.1898 |  | 219.6491 |  | 79.0031
02/08 22:00:00 | 21.4103 | 21.5241 | 21.0729 | 21.5842 | 22.722 | 20.9793 | 18.7862 | 13.2076 | 7.0574 | 7.801 | 12.2503 | 14.8481 | 9.1577 | 0.39201 | [14 empty] | 6.886 |  | 164.2389 |  |  |  | 44.4268 |  | 54.8926 |  | 140.6197 |  | 208.9795 |  | 76.8372
02/08 23:00:00 | 21.0519 | 21.1409 | 20.6935 | 21.1896 | 22.1869 | 20.5959 | 18.1471 | 12.9878 | 7.03 | 7.791 | 12.0745 | 14.5494 | 9.0646 | 0.37716 | [14 empty] | 8.4377 |  | 159.0278 |  |  |  | 44.2601 |  | 54.9653 |  | 136.8266 |  | 200.8524 |  | 75.4708
02/08 24:00:00 | 20.6536 | 20.7056 | 20.2817 | 20.7542 | 21.6703 | 20.1747 | 17.5727 | 12.6752 | 7.032 | 7.7411 | 11.8415 | 14.2444 | 8.9954 | 0.38097 | [14 empty] | 9.4919 |  | 151.1474 |  |  |  | 44.2364 |  | 54.1719 |  | 131.3429 |  | 192.194 |  | 74.2082
02/09 01:00:00 | 20.2704 | 20.2875 | 19.8983 | 20.3349 | 21.1668 | 19.7778 | 17.0393 | 12.3196 | 6.9229 | 7.7171 | 11.5287 | 13.8263 | 30.1001 | 0.39271 | [14 empty] | 10.4401 |  | 142.2506 |  |  |  | 42.643 |  | 53.6464 |  | 124.0101 |  | 180.4604 |  | 882.5272
02/09 02:00:00 | 19.9691 | 19.9658 | 19.6046 | 20.0032 | 20.8078 | 19.6356 | 16.4957 | 11.9692 | 6.8652 | 25.2633 | 11.2329 | 13.4396 | 44.581 | 0.42351 | [14 empty] | 12.0649 |  | 133.3034 |  |  |  | 41.4958 |  | 617.0159 |  | 116.8434 |  | 169.4188 |  | 1949.8871
02/09 03:00:00 | 19.6815 | 19.6609 | 19.4903 | 19.6888 | 20.4835 | 19.9203 | 16.0866 | 27.2965 | 26.3654 | 39.4474 | 30.4128 | 13.0828 | 34.196 | 0.42576 | [14 empty] | 12.9233 |  | 722.037 |  |  |  | 672.8648 |  | 1522.6919 |  | 899.2206 |  | 160.201 |  | 1140.4284
02/09 04:00:00 | 19.5498 | 19.5058 | 19.8131 | 19.5423 | 20.148 | 20.2501 | 15.6626 | 41.9637 | 39.8705 | 32.48 | 45.1837 | 13.3849 | 29.9527 | 0.43272 | [14 empty] | 15.1102 |  | 1724.8195 |  |  |  | 1555.3352 |  | 1027.0278 |  | 2002.6504 |  | 167.7596 |  | 871.4311
02/09 05:00:00 | 19.8192 | 19.7275 | 20.1817 | 19.7873 | 19.796 | 20.3586 | 15.2608 | 36.9491 | 39.4715 | 28.4713 | 46.3849 | 34.2144 | 30.0959 | 0.45929 | [14 empty] | 20.779 |  | 1331.5029 |  |  |  | 1521.9499 |  | 784.6711 |  | 2109.1602 |  | 1139.4048 |  | 878.3279
02/09 06:00:00 | 20.1341 | 20.0783 | 20.3305 | 20.1411 | 19.6032 | 20.3535 | 14.8576 | 32.8593 | 33.3624 | 23.0017 | 40.2784 | 47.5097 | 25.67 | 0.4456 | [14 empty] | 27.8411 |  | 1050.6467 |  |  |  | 1083.5132 |  | 508.7765 |  | 1586.6549 |  | 2215.0258 |  | 636.2686
02/09 07:00:00 | 20.2522 | 20.4127 | 20.3183 | 20.444 | 19.7954 | 20.2745 | 14.3912 | 25.5227 | 29.801 | 22.183 | 35.6209 | 46.4132 | 24.3093 | 0.46754 | [14 empty] | 34.3518 |  | 627.7615 |  |  |  | 860.4522 |  | 471.5606 |  | 1235.7559 |  | 2111.0063 |  | 568.4306
02/09 08:00:00 | 20.2104 | 20.6025 | 20.2551 | 20.5603 | 20.0986 | 20.1761 | 13.9445 | 46.0853 | 51.1041 | 27.7182 | 57.7517 | 63.8665 | 56.5509 | 0.48203 | [14 empty] | 39.2617 |  | 2079.6554 |  |  |  | 2562.5906 |  | 741.8097 |  | 3279.8147 |  | 4017.5883 |  | 3143.7186
02/09 09:00:00 | 20.2649 | 21.1915 | 20.1759 | 20.9728 | 21.4086 | 20.3715 | 13.6216 | 52.5656 | 46.3698 | 46.1347 | 58.6438 | 53.2695 | 59.5963 | 32.3957 | [14 empty] | 44.1339 |  | 406.8249 |  |  |  | 195.275 |  | 188.7594 |  | 688.9613 |  | 435.7133 |  | 739.8706
02/09 10:00:00 | 20.6917 | 22.3066 | 20.4671 | 22.0877 | 22.5956 | 21.5125 | 14.3252 | 54.7714 | 40.3002 | 53.5134 | 50.7392 | 48.3244 | 53.812 | 70.0997 | [14 empty] | 40.5328 |  | 234.9592 |  |  |  | 888.0127 |  | 275.1057 |  | 374.8306 |  | 474.1662 |  | 265.2906
02/09 11:00:00 | 21.4232 | 23.1657 | 21.5398 | 23.1938 | 23.1262 | 22.8232 | 16.24 | 52.7294 | 37.2281 | 49.4606 | 46.9516 | 45.6779 | 48.0037 | 77.5961 | [14 empty] | 26.8656 |  | 618.3521 |  |  |  | 1629.5768 |  | 791.6078 |  | 939.0878 |  | 1018.7683 |  | 875.7127
02/09 12:00:00 | 21.9865 | 23.6244 | 22.8712 | 23.7114 | 23.4375 | 23.5808 | 18.394 | 49.6217 | 30.9431 | 43.8025 | 39.6386 | 38.834 | 43.7511 | 79.5649 | [14 empty] | 12.9056 |  | 896.5934 |  |  |  | 2364.0782 |  | 1278.952 |  | 1594.1101 |  | 1659.0057 |  | 1282.6268
02/09 13:00:00 | 22.3241 | 23.8259 | 23.5274 | 23.8311 | 23.5683 | 23.8292 | 20.036 | 45.2762 | 33.5295 | 39.8571 | 40.789 | 39.5664 | 39.9415 | 75.0049 | [14 empty] | 5.2356 |  | 883.8 |  |  |  | 1720.2121 |  | 1235.3723 |  | 1170.7284 |  | 1255.8914 |  | 1229.4482
02/09 14:00:00 | 22.348 | 23.7849 | 23.4893 | 23.6497 | 23.4494 | 23.7231 | 21.2081 | 41.037 | 30.5316 | 36.7428 | 36.597 | 35.5448 | 36.3865 | 65.5486 | [14 empty] | 1.2994 |  | 600.8147 |  |  |  | 1226.188 |  | 829.7711 |  | 838.1933 |  | 900.2236 |  | 850.4261
02/09 15:00:00 | 22.3249 | 23.769 | 23.3708 | 23.4928 | 23.3481 | 23.6082 | 22.2198 | 38.7407 | 28.5022 | 34.4102 | 34.3031 | 33.3155 | 34.1337 | 67.5211 | [14 empty] | 0.011043 |  | 828.3158 |  |  |  | 1522.481 |  | 1096.3333 |  | 1103.4377 |  | 1170.0278 |  | 1114.7239
02/09 16:00:00 | 22.4545 | 23.902 | 23.4641 | 23.5242 | 23.4142 | 23.6751 | 22.5969 | 31.8655 | 26.8732 | 27.9619 | 32.5692 | 31.6314 | 32.4469 | 25.7234 | [14 empty] | 0.020271 |  | 37.7245 |  |  |  | 1.322 |  | 5.0109 |  | 46.864 |  | 34.9042 |  | 45.2056
02/09 17:00:00 | 22.4725 | 23.9902 | 23.4774 | 23.5002 | 23.4193 | 23.6968 | 22.1706 | 36.0602 | 25.5225 | 31.7896 | 30.9026 | 30.0608 | 30.7615 | 66.5694 | [14 empty] | 0.091154 |  | 930.8095 |  |  |  | 1684.8529 |  | 1209.6328 |  | 1272.1236 |  | 1332.8764 |  | 1282.2042
02/09 18:00:00 | 22.3178 | 23.8376 | 23.3039 | 23.2123 | 23.1632 | 23.4627 | 22.3226 | 32.8041 | 24.1914 | 29.0931 | 28.5239 | 27.7393 | 28.327 | 33.595 | [14 empty] | 2.3128e-05 |  | 0.62555 |  |  |  | 88.4279 |  | 20.2673 |  | 25.7156 |  | 34.2887 |  | 27.7514
02/09 19:00:00 | 22.0461 | 23.4993 | 23.011 | 22.7515 | 22.7282 | 23.0371 | 22.2298 | 31.3922 | 23.1489 | 27.7694 | 27.2352 | 26.4258 | 27.0177 | 54.9885 | [14 empty] | 0.033781 |  | 556.7808 |  |  |  | 1013.7559 |  | 740.8775 |  | 770.2453 |  | 815.8268 |  | 782.363
02/09 20:00:00 | 21.5285 | 22.9233 | 22.4775 | 22.0848 | 22.0051 | 22.3928 | 22.0945 | 34.3118 | 22.2932 | 26.6486 | 26.1953 | 25.4793 | 25.9758 | 75.8784 | [14 empty] | 0.32029 |  | 1727.788 |  |  |  | 2871.3801 |  | 2423.5795 |  | 2468.4097 |  | 2540.0747 |  | 2490.2705
02/09 21:00:00 | 20.9055 | 22.2836 | 21.8205 | 21.385 | 21.1646 | 21.7041 | 22.1555 | 28.5305 | 16.4872 | 20.0648 | 20.0592 | 19.5388 | 19.8988 | 5.7988 | [14 empty] | 1.5623 |  | 516.7307 |  |  |  | 114.2404 |  | 203.519 |  | 203.3596 |  | 188.7879 |  | 198.8103
02/09 22:00:00 | 20.6003 | 21.6885 | 21.3533 | 20.7554 | 20.4537 | 21.0798 | 21.1895 | 25.7052 | 16.0941 | 19.5276 | 19.6863 | 19.1893 | 19.5288 | 26.5591 | [14 empty] | 0.34726 |  | 0.72917 |  |  |  | 109.5169 |  | 49.4414 |  | 47.2357 |  | 54.3144 |  | 49.4255
02/09 23:00:00 | 20.2839 | 21.0875 | 20.9506 | 20.1369 | 19.7921 | 20.4585 | 20.5102 | 24.5967 | 15.6715 | 18.7423 | 18.7187 | 40.8142 | 18.5672 | 31.1792 | [14 empty] | 0.051212 |  | 43.33 |  |  |  | 240.4906 |  | 154.6778 |  | 155.265 |  | 92.833 |  | 159.0627
02/09 24:00:00 | 19.9256 | 20.5462 | 20.5302 | 19.5859 | 19.4215 | 19.8062 | 20.1107 | 23.4596 | 15.1824 | 17.9933 | 38.0011 | 48.5546 | 17.8788 | 32.3644 | [14 empty] | 0.034243 |  | 79.2957 |  |  |  | 295.2229 |  | 206.5297 |  | 31.7721 |  | 262.1212 |  | 209.8326
02/10 01:00:00 | 19.5814 | 20.0758 | 20.14 | 19.2944 | 19.661 | 19.3495 | 19.8564 | 35.1448 | 14.7796 | 17.5742 | 47.7253 | 48.0617 | 35.7202 | 35.6453 | [14 empty] | 0.075659 |  | 0.25052 |  |  |  | 435.3803 |  | 326.5667 |  | 145.9265 |  | 154.1673 |  | 0.0056118
02/10 02:00:00 | 19.4364 | 19.7422 | 19.8357 | 19.529 | 20.0086 | 19.1754 | 19.7054 | 36.7063 | 29.9067 | 16.9028 | 47.1872 | 41.1618 | 48.3814 | 36.1199 | [14 empty] | 0.07237 |  | 0.34392 |  |  |  | 38.6042 |  | 369.2955 |  | 122.4863 |  | 25.4206 |  | 150.3438
02/10 03:00:00 | 19.4649 | 19.574 | 19.5459 | 19.8433 | 20.2198 | 19.4247 | 19.6787 | 39.883 | 40.3173 | 30.8645 | 41.6111 | 37.4813 | 47.6863 | 35.56 | [14 empty] | 0.045694 |  | 18.6885 |  |  |  | 22.6324 |  | 22.0475 |  | 36.6158 |  | 3.6914 |  | 147.0494
02/10 04:00:00 | 19.5305 | 19.7165 | 19.4044 | 20.0563 | 20.2217 | 19.7627 | 19.5876 | 41.6701 | 40.1235 | 42.1332 | 38.3334 | 36.6003 | 48.1605 | 36.5698 | [14 empty] | 0.0032582 |  | 26.0124 |  |  |  | 12.6287 |  | 30.9511 |  | 3.1103 |  | 0.00092984 |  | 134.3441
02/10 05:00:00 | 19.5951 | 19.9539 | 19.6218 | 20.0856 | 20.1151 | 20.0282 | 19.449 | 42.649 | 34.9145 | 43.4882 | 37.293 | 35.3765 | 43.8831 | 37.2334 | [14 empty] | 0.021349 |  | 29.3293 |  |  |  | 5.3772 |  | 39.1229 |  | 0.0035628 |  | 3.4479 |  | 44.2197
02/10 06:00:00 | 19.6501 | 20.1638 | 19.9263 | 20.0065 | 19.9313 | 20.2026 | 19.3721 | 44.1251 | 31.5946 | 38.4051 | 34.7652 | 32.9878 | 39.5532 | 38.9746 | [14 empty] | 0.077297 |  | 26.5278 |  |  |  | 54.4638 |  | 0.32436 |  | 17.7188 |  | 35.8424 |  | 0.3348
02/10 07:00:00 | 19.7225 | 20.2491 | 20.1792 | 19.8602 | 19.6993 | 20.2241 | 19.2986 | 47.9746 | 30.3664 | 28.2481 | 32.4517 | 41.456 | 37.1557 | 39.0127 | [14 empty] | 0.17968 |  | 80.3159 |  |  |  | 74.758 |  | 115.8752 |  | 43.0466 |  | 5.9698 |  | 3.4484
02/10 08:00:00 | 19.9289 | 20.2568 | 20.192 | 19.6649 | 19.5325 | 20.155 | 19.6091 | 55.3078 | 52.0763 | 51.1218 | 57.9494 | 66.6916 | 60.9891 | 77.1098 | [14 empty] | 0.1023 |  | 475.3273 |  |  |  | 626.6743 |  | 675.3756 |  | 367.1211 |  | 108.539 |  | 259.8749
02/10 09:00:00 | 20.0943 | 20.5859 | 20.3219 | 19.716 | 20.22 | 20.4565 | 20.9001 | 54.8003 | 52.5856 | 54.0477 | 59.7768 | 60.5075 | 59.7008 | 74.2119 | [14 empty] | 0.6493 |  | 376.81 |  |  |  | 467.7 |  | 406.596 |  | 208.3739 |  | 187.8101 |  | 210.5725
02/10 10:00:00 | 20.4893 | 21.6517 | 21.0726 | 20.6777 | 21.2836 | 21.4206 | 22.3007 | 53.3681 | 46.0948 | 49.8972 | 57.5824 | 54.7146 | 53.6352 | 25.0297 | [14 empty] | 3.2811 |  | 803.0647 |  |  |  | 443.7406 |  | 618.3931 |  | 1059.678 |  | 881.1949 |  | 818.2725
02/10 11:00:00 | 21.3399 | 23.2493 | 22.4718 | 22.273 | 22.5984 | 22.9194 | 22.4877 | 50.4621 | 39.2441 | 44.3103 | 49.5817 | 47.9882 | 46.9193 | 10.9212 | [14 empty] | 1.3176 |  | 1563.4785 |  |  |  | 802.1873 |  | 1114.8282 |  | 1494.6323 |  | 1373.9636 |  | 1295.8626
02/10 12:00:00 | 22.5318 | 24.649 | 23.711 | 23.7246 | 23.785 | 24.2538 | 22.3207 | 44.274 | 34.8268 | 39.4244 | 42.5936 | 41.5052 | 40.618 | 16.5661 | [14 empty] | 0.044528 |  | 767.7278 |  |  |  | 333.4538 |  | 522.5028 |  | 677.4291 |  | 621.9567 |  | 578.4912
02/10 13:00:00 | 23.3555 | 25.4084 | 24.4137 | 24.3766 | 24.4253 | 24.9075 | 22.2267 | 41.6751 | 33.2372 | 36.9747 | 40.3013 | 39.5607 | 38.6476 | 27.7294 | [14 empty] | 1.274 |  | 194.481 |  |  |  | 30.3349 |  | 85.4744 |  | 158.0523 |  | 139.9797 |  | 119.2066
02/10 14:00:00 | 23.306 | 25.5062 | 24.4288 | 24.3861 | 24.4685 | 24.9365 | 22.1607 | 39.6032 | 31.3393 | 35.0122 | 38.2315 | 37.6982 | 36.6407 | 41.9417 | [14 empty] | 1.3118 |  | 5.4685 |  |  |  | 112.4091 |  | 48.0177 |  | 13.7649 |  | 18.007 |  | 28.1005
02/10 15:00:00 | 23.2105 | 25.4721 | 24.3675 | 24.3184 | 24.4227 | 24.903 | 22.1286 | 37.5342 | 29.6613 | 33.0027 | 35.7735 | 35.2008 | 34.5321 | 54.4963 | [14 empty] | 1.1704 |  | 287.7108 |  |  |  | 616.7737 |  | 461.9711 |  | 350.5427 |  | 372.314 |  | 398.5696
02/10 16:00:00 | 23.3593 | 25.6599 | 24.5741 | 24.4925 | 24.6126 | 25.0912 | 22.3501 | 37.3353 | 28.9992 | 32.0746 | 35.2404 | 34.655 | 34.3474 | 29.8246 | [14 empty] | 1.0186 |  | 56.4105 |  |  |  | 0.68125 |  | 5.0623 |  | 29.3306 |  | 23.3325 |  | 20.4557
02/10 17:00:00 | 23.391 | 25.7548 | 24.6527 | 24.5099 | 24.6492 | 25.1322 | 22.268 | 34.6248 | 28.0019 | 30.0877 | 32.595 | 32.0923 | 31.7454 | 35.5371 | [14 empty] | 1.2611 |  | 0.83218 |  |  |  | 56.7794 |  | 29.6961 |  | 8.6555 |  | 11.8665 |  | 14.3771
02/10 18:00:00 | 23.2116 | 25.6288 | 24.5142 | 24.3023 | 24.4463 | 24.939 | 22.2212 | 30.2192 | 25.8694 | 26.9816 | 28.3644 | 27.9677 | 27.5782 | 52.9216 | [14 empty] | 0.98085 |  | 515.3995 |  |  |  | 731.82 |  | 672.8794 |  | 603.0535 |  | 622.6938 |  | 642.2838
02/10 19:00:00 | 23.0044 | 25.4601 | 24.3204 | 24.0248 | 24.1803 | 24.6774 | 22.3347 | 30.6529 | 24.8107 | 26.6469 | 28.5023 | 28.098 | 27.7885 | 28.6673 | [14 empty] | 0.44841 |  | 3.9425 |  |  |  | 14.8734 |  | 4.0822 |  | 0.027244 |  | 0.32415 |  | 0.77232
02/10 20:00:00 | 22.5447 | 24.9701 | 23.8546 | 23.4428 | 23.603 | 24.1056 | 22.2143 | 28.9453 | 23.9488 | 25.4753 | 26.9818 | 26.5592 | 26.2794 | 49.8399 | [14 empty] | 0.10917 |  | 436.5828 |  |  |  | 670.3461 |  | 593.6336 |  | 522.4911 |  | 541.9882 |  | 555.0973
02/10 21:00:00 | 21.9997 | 24.4083 | 23.293 | 22.8561 | 22.9131 | 23.4177 | 22.2472 | 22.7771 | 17.7042 | 19.3445 | 20.8662 | 20.5281 | 20.4268 | 5.0511 | [14 empty] | 0.061229 |  | 314.2121 |  |  |  | 160.1 |  | 204.3013 |  | 250.1185 |  | 239.5365 |  | 236.4122
02/10 22:00:00 | 21.6147 | 23.918 | 22.9002 | 22.3558 | 22.326 | 22.9254 | 21.6091 | 22.0833 | 17.1879 | 18.7443 | 20.2805 | 19.9901 | 19.857 | 20.5474 | [14 empty] | 3.0916e-05 |  | 2.3589 |  |  |  | 11.2859 |  | 3.2511 |  | 0.071232 |  | 0.31062 |  | 0.47661
02/10 23:00:00 | 21.3032 | 23.4358 | 22.5796 | 21.8857 | 21.7914 | 22.4509 | 21.2415 | 20.7311 | 16.5608 | 17.755 | 19.0238 | 18.7944 | 18.6303 | 23.1163 | [14 empty] | 0.0038143 |  | 5.6893 |  |  |  | 42.9741 |  | 28.7429 |  | 16.7483 |  | 18.6786 |  | 20.124
02/10 24:00:00 | 21.0258 | 23.0259 | 22.3165 | 21.4952 | 21.3548 | 21.9824 | 21.0328 | 19.5356 | 15.8626 | 14.2359 | 18.0033 | 17.8396 | 17.6809 | 23.9115 | [14 empty] | 4.9722e-05 |  | 19.1484 |  |  |  | 64.7839 |  | 93.6167 |  | 34.9066 |  | 36.8682 |  | 38.8205
02/11 01:00:00 | 20.7899 | 22.6992 | 22.1202 | 21.241 | 21.0479 | 21.6713 | 20.8884 | 14.8964 | 15.0437 | 13.4552 | 16.3939 | 16.2389 | 16.0778 | 25.0491 | [14 empty] | 0.0096899 |  | 103.0776 |  |  |  | 100.1092 |  | 134.4192 |  | 74.9126 |  | 77.6204 |  | 80.4853
02/11 02:00:00 | 20.6206 | 22.4666 | 21.9914 | 21.0298 | 20.7789 | 21.4552 | 20.8246 | 13.8013 | 14.2428 | 12.6013 | 15.0626 | 14.9424 | 14.787 | 24.9417 | [14 empty] | 0.041631 |  | 124.1079 |  |  |  | 114.4652 |  | 152.2855 |  | 97.5957 |  | 99.9857 |  | 103.1183
02/11 03:00:00 | 20.5117 | 22.2755 | 21.8717 | 20.8351 | 20.5828 | 21.2711 | 20.8023 | 14.4519 | 13.8177 | 12.7266 | 15.3124 | 15.1916 | 15.0082 | 25.2696 | [14 empty] | 0.084442 |  | 117.0234 |  |  |  | 131.1476 |  | 157.3271 |  | 99.1459 |  | 101.5666 |  | 105.2974
02/11 04:00:00 | 20.3996 | 22.0809 | 21.7465 | 20.6345 | 20.3926 | 21.0756 | 20.8166 | 13.0443 | 11.4124 | 11.8528 | 12.3591 | 32.3959 | 12.2525 | 23.7364 | [14 empty] | 0.17386 |  | 114.3196 |  |  |  | 151.8793 |  | 141.2183 |  | 129.442 |  | 74.9875 |  | 131.8793
02/11 05:00:00 | 20.2939 | 21.9251 | 21.6275 | 20.4771 | 20.3602 | 20.9209 | 20.8601 | 21.0997 | 13.101 | 11.4097 | 30.9398 | 44.015 | 13.3648 | 25.1445 | [14 empty] | 0.32065 |  | 16.3604 |  |  |  | 145.0446 |  | 188.6431 |  | 33.5852 |  | 356.0978 |  | 138.7613
02/11 06:00:00 | 20.2778 | 21.7786 | 21.5025 | 20.4758 | 20.6763 | 20.7684 | 20.8951 | 40.0083 | 12.2082 | 10.891 | 42.367 | 34.076 | 12.3966 | 23.9637 | [14 empty] | 0.3811 |  | 257.4293 |  |  |  | 138.1911 |  | 170.8954 |  | 338.6818 |  | 102.2591 |  | 133.797
02/11 07:00:00 | 20.6003 | 21.5887 | 21.3882 | 20.8022 | 21.043 | 20.5747 | 20.9075 | 34.9896 | 10.2026 | 10.732 | 34.5645 | 29.6759 | 10.9313 | 23.8225 | [14 empty] | 0.094363 |  | 124.7038 |  |  |  | 185.5035 |  | 171.3604 |  | 115.3907 |  | 34.2626 |  | 166.1825
02/11 08:00:00 | 21.0068 | 21.435 | 21.2797 | 21.1821 | 21.2424 | 20.4174 | 20.9378 | 31.1073 | 10.1337 | 10.4253 | 30.0177 | 25.8952 | 10.7679 | 23.3241 | [14 empty] | 0.0047666 |  | 60.5787 |  |  |  | 173.9864 |  | 166.3779 |  | 44.8038 |  | 6.6108 |  | 157.6591
02/11 09:00:00 | 21.2363 | 21.3305 | 21.1625 | 21.3805 | 21.3043 | 20.305 | 21.4783 | 30.2738 | 13.4301 | 13.2324 | 53.6222 | 56.4979 | 41.2016 | 80.4039 | [14 empty] | 0.058549 |  | 2513.0291 |  |  |  | 4485.4891 |  | 4512.0115 |  | 717.2597 |  | 571.4969 |  | 1536.8211
02/11 10:00:00 | 21.2861 | 21.2156 | 21.054 | 21.8796 | 21.8379 | 20.4256 | 22.7466 | 44.1512 | 39.9836 | 34.4558 | 44.4608 | 43.994 | 58.4762 | 16.4742 | [14 empty] | 2.1331 |  | 766.0158 |  |  |  | 552.6911 |  | 323.337 |  | 783.2451 |  | 757.3363 |  | 1764.1615
02/11 11:00:00 | 21.4919 | 21.3384 | 21.1618 | 23.0019 | 22.9763 | 21.4129 | 23.123 | 48.3236 | 50.8768 | 48.422 | 36.9482 | 35.7057 | 53.6915 | 6.9942 | [14 empty] | 2.6603 |  | 1708.1154 |  |  |  | 1925.6859 |  | 1716.2633 |  | 897.2439 |  | 824.3491 |  | 2180.634
02/11 12:00:00 | 21.981 | 22.4588 | 21.8436 | 23.5819 | 23.4862 | 23.2441 | 23.2946 | 40.2226 | 34.1864 | 36.3367 | 32.5858 | 31.6144 | 39.9597 | 3.1218 | [14 empty] | 1.7256 |  | 1376.4622 |  |  |  | 965.0037 |  | 1103.2241 |  | 868.1268 |  | 811.828 |  | 1357.0293
02/11 13:00:00 | 22.9811 | 24.2761 | 23.3303 | 23.9157 | 23.8576 | 24.7041 | 23.3032 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0077 | [14 empty] | 0.10374 |  | 9.0463 |  |  |  | 9.0463 |  | 9.0463 |  | 9.0463 |  | 9.0463 |  | 9.0463
02/11 14:00:00 | 22.8171 | 24.6431 | 23.4865 | 23.6776 | 23.6918 | 24.6243 | 23.3237 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9849 | [14 empty] | 0.25668 |  | 8.9095 |  |  |  | 8.9095 |  | 8.9095 |  | 8.9095 |  | 8.9095 |  | 8.9095
02/11 15:00:00 | 22.1544 | 24.3306 | 23.0651 | 23.3093 | 23.363 | 24.1822 | 23.3249 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0004 | [14 empty] | 1.37 |  | 9.0024 |  |  |  | 9.0024 |  | 9.0024 |  | 9.0024 |  | 9.0024 |  | 9.0024
02/11 16:00:00 | 21.7876 | 24.1468 | 22.8691 | 23.1101 | 23.1697 | 23.9714 | 23.3894 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9058 | [14 empty] | 2.5656 |  | 8.4439 |  |  |  | 8.4439 |  | 8.4439 |  | 8.4439 |  | 8.4439 |  | 8.4439
02/11 17:00:00 | 21.6464 | 24.0846 | 22.8239 | 23.023 | 23.08 | 23.9112 | 23.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8733 | [14 empty] | 2.516 |  | 8.2557 |  |  |  | 8.2557 |  | 8.2557 |  | 8.2557 |  | 8.2557 |  | 8.2557
02/11 18:00:00 | 21.5794 | 24.0739 | 22.8369 | 22.9935 | 23.0435 | 23.9065 | 22.9046 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9533 | [14 empty] | 1.756 |  | 8.7221 |  |  |  | 8.7221 |  | 8.7221 |  | 8.7221 |  | 8.7221 |  | 8.7221
02/11 19:00:00 | 21.4892 | 24.0256 | 22.8391 | 22.9227 | 22.9494 | 23.858 | 22.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 34.4909 | [14 empty] | 1.583 |  | 1189.6189 |  |  |  | 1189.6189 |  | 1189.6189 |  | 1189.6189 |  | 1189.6189 |  | 1189.6189
02/11 20:00:00 | 21.2458 | 23.8005 | 22.7167 | 22.6743 | 22.6532 | 23.602 | 22.9065 | 0 | 0 | 0 | 0 | 0 | 0 | 3.413 | [14 empty] | 2.7578 |  | 11.6488 |  |  |  | 11.6488 |  | 11.6488 |  | 11.6488 |  | 11.6488 |  | 11.6488
02/11 21:00:00 | 21.0282 | 23.5488 | 22.5676 | 22.4113 | 22.364 | 23.333 | 22.6871 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2248 | [14 empty] | 2.7518 |  | 104.5459 |  |  |  | 104.5459 |  | 104.5459 |  | 104.5459 |  | 104.5459 |  | 104.5459
02/11 22:00:00 | 20.8702 | 23.3233 | 22.4308 | 22.1698 | 22.1145 | 23.0935 | 22.5092 | 0 | 0 | 0 | 0 | 0 | 0 | 11.021 | [14 empty] | 2.6863 |  | 121.4616 |  |  |  | 121.4616 |  | 121.4616 |  | 121.4616 |  | 121.4616 |  | 121.4616
02/11 23:00:00 | 20.6817 | 23.0501 | 22.2567 | 21.8898 | 21.8196 | 22.8026 | 22.4123 | 0 | 0 | 0 | 0 | 0 | 0 | 11.3216 | [14 empty] | 2.995 |  | 128.1797 |  |  |  | 128.1797 |  | 128.1797 |  | 128.1797 |  | 128.1797 |  | 128.1797
02/11 24:00:00 | 20.4752 | 22.7486 | 22.0623 | 21.6451 | 21.5023 | 22.4837 | 22.2974 | 46.7948 | 38.3063 | 36.1712 | 37.4291 | 38.9238 | 45.997 | 12.7134 | [14 empty] | 3.3201 |  | 1161.5448 |  |  |  | 654.996 |  | 550.2689 |  | 610.8659 |  | 686.9873 |  | 1107.7979
02/12 01:00:00 | 21.2195 | 23.0115 | 22.6085 | 21.9882 | 21.7564 | 23.0177 | 22.2004 | 36.5909 | 23.599 | 25.2853 | 25.0202 | 24.5283 | 29.8819 | 12.4385 | [14 empty] | 0.96219 |  | 583.3367 |  |  |  | 124.5565 |  | 165.0397 |  | 158.2984 |  | 146.1633 |  | 304.2707
02/12 02:00:00 | 22.2189 | 23.3258 | 23.0941 | 22.2793 | 22.0385 | 23.5168 | 22.1288 | 32.8983 | 21.5129 | 23.3859 | 22.9563 | 22.3057 | 27.3388 | 13.4921 | [14 empty] | 0.0081234 |  | 376.6009 |  |  |  | 64.3346 |  | 97.8886 |  | 89.572 |  | 77.6807 |  | 191.7318
02/12 03:00:00 | 22.6535 | 23.5012 | 23.3113 | 22.4134 | 22.1686 | 23.7155 | 22.0849 | 25.3608 | 20.5003 | 18.5075 | 22.0497 | 21.4297 | 26.1895 | 13.7442 | [14 empty] | 0.32328 |  | 134.9465 |  |  |  | 45.6447 |  | 22.6887 |  | 68.9816 |  | 59.0676 |  | 154.8852
02/12 04:00:00 | 22.7441 | 23.6025 | 23.3621 | 22.4655 | 22.2116 | 23.7871 | 22.0135 | 24.4709 | 19.5756 | 18.0542 | 18.229 | 20.289 | 24.7513 | 14.57 | [14 empty] | 0.53376 |  | 98.0295 |  |  |  | 25.0563 |  | 12.1402 |  | 13.3884 |  | 32.7078 |  | 103.6607
02/12 05:00:00 | 22.751 | 23.6485 | 23.3555 | 22.4495 | 22.1977 | 23.79 | 21.9898 | 23.5579 | 16.0524 | 17.4238 | 17.721 | 17.2766 | 23.5 | 14.3403 | [14 empty] | 0.5794 |  | 84.9638 |  |  |  | 2.9312 |  | 9.5075 |  | 11.4287 |  | 8.6215 |  | 83.8992
02/12 06:00:00 | 22.7395 | 23.6357 | 23.3323 | 22.4091 | 22.1444 | 23.7427 | 21.967 | 22.6398 | 15.8005 | 16.7705 | 17.0488 | 16.7991 | 19.7387 | 15.1459 | [14 empty] | 0.59677 |  | 56.1576 |  |  |  | 0.42853 |  | 2.6392 |  | 3.6208 |  | 2.733 |  | 21.0936
02/12 07:00:00 | 22.7217 | 23.6071 | 23.3031 | 22.3595 | 22.0887 | 23.6692 | 21.9267 | 22.0345 | 15.3314 | 16.2586 | 16.5672 | 16.3547 | 19.4256 | 15.1407 | [14 empty] | 0.63195 |  | 47.5244 |  |  |  | 0.036398 |  | 1.2498 |  | 2.035 |  | 1.4739 |  | 18.3603
02/12 08:00:00 | 22.6964 | 23.5695 | 23.2675 | 22.3024 | 22.0235 | 23.6018 | 21.9331 | 21.2768 | 14.8146 | 15.7031 | 15.9804 | 15.7685 | 18.7575 | 14.8799 | [14 empty] | 0.58262 |  | 40.9194 |  |  |  | 0.0042621 |  | 0.67769 |  | 1.211 |  | 0.78953 |  | 15.0356
02/12 09:00:00 | 22.6761 | 23.5338 | 23.2378 | 22.2498 | 21.9636 | 23.538 | 22.2817 | 24.4782 | 22.3295 | 19.4722 | 22.0378 | 22.1671 | 26.504 | 42.9679 | [14 empty] | 0.15558 |  | 341.8672 |  |  |  | 425.9446 |  | 552.047 |  | 438.0705 |  | 432.6727 |  | 271.0586
02/12 10:00:00 | 22.6577 | 23.5348 | 23.2142 | 22.2156 | 21.9363 | 23.5275 | 22.8534 | 0 | 0 | 0 | 0 | 0 | 0 | 16.8863 | [14 empty] | 0.038287 |  | 285.147 |  |  |  | 285.147 |  | 285.147 |  | 285.147 |  | 285.147 |  | 285.147
02/12 11:00:00 | 22.2827 | 23.3713 | 22.9959 | 22.0016 | 21.753 | 23.3077 | 23.0618 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5082 | [14 empty] | 0.60696 |  | 12.3072 |  |  |  | 12.3072 |  | 12.3072 |  | 12.3072 |  | 12.3072 |  | 12.3072
02/12 12:00:00 | 21.931 | 23.1743 | 22.7711 | 21.792 | 21.572 | 23.0743 | 23.0909 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8628 | [14 empty] | 1.3453 |  | 8.1959 |  |  |  | 8.1959 |  | 8.1959 |  | 8.1959 |  | 8.1959 |  | 8.1959
02/12 13:00:00 | 21.7225 | 23.0219 | 22.6151 | 21.6422 | 21.432 | 22.8985 | 23.004 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0682 | [14 empty] | 1.6424 |  | 9.4141 |  |  |  | 9.4141 |  | 9.4141 |  | 9.4141 |  | 9.4141 |  | 9.4141
02/12 14:00:00 | 21.5839 | 22.9086 | 22.5007 | 21.5296 | 21.3215 | 22.7663 | 22.7082 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6961 | [14 empty] | 1.2641 |  | 942.2532 |  |  |  | 942.2532 |  | 942.2532 |  | 942.2532 |  | 942.2532 |  | 942.2532
02/12 15:00:00 | 21.4157 | 22.7686 | 22.3535 | 21.3819 | 21.1743 | 22.6022 | 22.8811 | 45.6723 | 29.6445 | 28.1397 | 49.1076 | 52.7721 | 34.3438 | 6.4712 | [14 empty] | 2.1472 |  | 1536.7272 |  |  |  | 537.0056 |  | 469.5268 |  | 1817.8637 |  | 2143.7809 |  | 776.884
02/12 16:00:00 | 21.6477 | 22.7915 | 22.4075 | 21.5394 | 21.3434 | 22.6536 | 22.9089 | 48.0618 | 18.9375 | 20.1668 | 55.756 | 57.8233 | 22.0227 | 3.5947 | [14 empty] | 1.5906 |  | 1977.324 |  |  |  | 235.4024 |  | 274.6331 |  | 2720.7968 |  | 2940.7454 |  | 339.5899
02/12 17:00:00 | 22.2417 | 22.8784 | 22.5124 | 22.8478 | 22.8641 | 22.7812 | 22.6704 | 41.1473 | 17.0452 | 15.8054 | 39.6887 | 39.6534 | 19.6214 | 30.7689 | [14 empty] | 0.18375 |  | 107.7119 |  |  |  | 188.3375 |  | 223.9049 |  | 79.5628 |  | 78.9355 |  | 124.2649
02/12 18:00:00 | 22.9804 | 22.9857 | 22.5879 | 24.41 | 24.4612 | 22.9092 | 22.7454 | 37.0504 | 16.2032 | 18.1682 | 35.5079 | 34.7004 | 18.6178 | 23.1414 | [14 empty] | 0.055231 |  | 193.4587 |  |  |  | 48.139 |  | 24.7331 |  | 152.9301 |  | 133.61 |  | 20.4636
02/12 19:00:00 | 23.3062 | 23.0035 | 22.5927 | 24.8629 | 24.8423 | 22.9109 | 22.7749 | 36.3126 | 15.7959 | 21.449 | 35.1521 | 34.7828 | 18.6662 | 26.0939 | [14 empty] | 0.28226 |  | 104.4217 |  |  |  | 106.0497 |  | 21.5757 |  | 82.0503 |  | 75.4968 |  | 55.1714
02/12 20:00:00 | 23.4271 | 22.9413 | 22.5648 | 24.8389 | 24.8159 | 22.7949 | 22.3683 | 23.3431 | 11.6 | 16.3751 | 25.8847 | 25.4745 | 14.1934 | 7.9464 | [14 empty] | 1.1211 |  | 237.0587 |  |  |  | 13.3484 |  | 71.0429 |  | 321.7817 |  | 307.2338 |  | 39.0248
02/12 21:00:00 | 23.4072 | 22.8478 | 22.5777 | 24.738 | 24.6784 | 22.6547 | 20.8552 | 28.1001 | 11.2574 | 14.6906 | 24.7562 | 24.4569 | 13.819 | 30.8062 | [14 empty] | 6.5128 |  | 7.3232 |  |  |  | 382.1539 |  | 259.7134 |  | 36.6029 |  | 40.3133 |  | 288.5662
02/12 22:00:00 | 23.3756 | 22.7016 | 22.4957 | 24.4692 | 24.3496 | 22.4881 | 19.9029 | 26.345 | 11.0467 | 14.4395 | 23.7845 | 23.503 | 13.4399 | 35.1958 | [14 empty] | 12.0602 |  | 78.3366 |  |  |  | 583.176 |  | 430.8219 |  | 130.2163 |  | 136.7196 |  | 473.3167
02/12 23:00:00 | 23.272 | 22.5093 | 22.3415 | 24.1319 | 23.9494 | 22.2673 | 19.11 | 25.5153 | 10.8951 | 14.2495 | 23.1733 | 22.9179 | 13.3692 | 42.4817 | [14 empty] | 17.3221 |  | 287.857 |  |  |  | 997.7137 |  | 797.0554 |  | 372.8109 |  | 382.7394 |  | 847.5357
02/12 24:00:00 | 23.1118 | 22.242 | 22.1131 | 23.7579 | 23.5081 | 21.9681 | 18.6777 | 23.819 | 10.5892 | 13.5606 | 21.7205 | 21.5471 | 12.5658 | 42.8769 | [14 empty] | 19.6612 |  | 363.2039 |  |  |  | 1042.4989 |  | 859.4469 |  | 447.594 |  | 454.9602 |  | 918.7668
02/13 01:00:00 | 22.9123 | 21.9669 | 21.8709 | 23.3674 | 23.1299 | 21.6631 | 18.5208 | 23.1773 | 10.3558 | 13.2391 | 21.248 | 21.0236 | 12.4221 | 46.9369 | [14 empty] | 19.2847 |  | 564.5202 |  |  |  | 1338.1752 |  | 1135.54 |  | 659.9194 |  | 671.4984 |  | 1191.272
02/13 02:00:00 | 22.7188 | 21.7448 | 21.669 | 23.0707 | 22.776 | 21.3998 | 18.2764 | 22.7216 | 10.2339 | 13.1084 | 20.89 | 20.7246 | 12.4819 | 48.5223 | [14 empty] | 19.7352 |  | 665.6771 |  |  |  | 1466.0031 |  | 1254.1417 |  | 763.5448 |  | 772.7135 |  | 1298.9143
02/13 03:00:00 | 22.4809 | 21.4935 | 21.4279 | 22.7367 | 22.4467 | 21.1072 | 18.207 | 22.0715 | 10.1072 | 12.8842 | 20.351 | 20.2088 | 12.3532 | 45.8144 | [14 empty] | 18.2666 |  | 563.7258 |  |  |  | 1275.0062 |  | 1084.4024 |  | 648.3886 |  | 655.6464 |  | 1119.6532
02/13 04:00:00 | 22.2255 | 21.2325 | 21.1748 | 22.4447 | 22.0889 | 20.8099 | 18.2908 | 21.2068 | 9.9039 | 12.5326 | 19.617 | 19.4838 | 12.0124 | 47.9846 | [14 empty] | 15.4813 |  | 717.0504 |  |  |  | 1450.1337 |  | 1256.8437 |  | 804.7186 |  | 812.2932 |  | 1293.9966
02/13 05:00:00 | 21.9617 | 20.9719 | 20.9231 | 22.1634 | 21.795 | 20.5172 | 18.7209 | 20.4123 | 9.7145 | 12.2269 | 18.911 | 18.7965 | 11.9227 | 39.2613 | [14 empty] | 10.5025 |  | 355.2869 |  |  |  | 873.0138 |  | 730.8586 |  | 414.1356 |  | 418.8066 |  | 747.399
02/13 06:00:00 | 21.6652 | 20.6855 | 20.6401 | 21.8396 | 21.4275 | 20.1995 | 19.1289 | 20.2557 | 9.6034 | 10.4581 | 18.8014 | 18.6968 | 32.6266 | 36.8931 | [14 empty] | 6.4329 |  | 276.8009 |  |  |  | 744.7234 |  | 698.8055 |  | 327.3078 |  | 331.1046 |  | 18.203
02/13 07:00:00 | 21.3715 | 20.4025 | 20.4116 | 21.5115 | 21.0738 | 20.0601 | 19.2507 | 19.45 | 27.3435 | 10.3543 | 18.0874 | 18.0143 | 46.0126 | 37.9068 | [14 empty] | 4.4975 |  | 340.6529 |  |  |  | 111.5818 |  | 759.139 |  | 392.8097 |  | 395.7098 |  | 65.7041
02/13 08:00:00 | 21.0771 | 20.266 | 20.2311 | 21.1787 | 20.7524 | 20.3198 | 19.7509 | 19.1228 | 54.7326 | 25.57 | 43.0916 | 46.1239 | 62.2742 | 82.8101 | [14 empty] | 1.7588 |  | 4056.0701 |  |  |  | 788.3439 |  | 3276.4267 |  | 1577.5566 |  | 1345.8795 |  | 421.7218
02/13 09:00:00 | 20.853 | 20.8851 | 20.1896 | 21.0557 | 20.6685 | 21.5951 | 20.9851 | 40.9972 | 51.3411 | 52.8102 | 59.9444 | 62.3597 | 57.5655 | 68.212 | [14 empty] | 0.017467 |  | 740.646 |  |  |  | 284.6265 |  | 237.2144 |  | 68.3535 |  | 34.2495 |  | 113.3477
02/13 10:00:00 | 20.9921 | 22.4469 | 20.8774 | 22.0414 | 21.7372 | 23.0941 | 21.9944 | 49.669 | 40.0219 | 52.2478 | 47.7773 | 47.6364 | 47.5173 | 57.0945 | [14 empty] | 1.0045 |  | 55.139 |  |  |  | 291.4751 |  | 23.4909 |  | 86.8117 |  | 89.4565 |  | 91.7235
02/13 11:00:00 | 21.6859 | 24.1186 | 22.4816 | 23.7535 | 23.5812 | 24.1574 | 22.476 | 51.7944 | 35.6102 | 44.0858 | 41.4813 | 41.0298 | 43.0363 | 20.4517 | [14 empty] | 0.6243 |  | 982.36 |  |  |  | 229.7799 |  | 558.5698 |  | 442.2448 |  | 423.455 |  | 510.0624
02/13 12:00:00 | 22.564 | 24.9189 | 23.899 | 24.4844 | 24.4825 | 24.7173 | 22.5695 | 45.3287 | 33.2658 | 39.1809 | 37.8591 | 37.645 | 40.0084 | 29.4952 | [14 empty] | 3.0184e-05 |  | 250.7 |  |  |  | 14.2173 |  | 93.8125 |  | 69.9558 |  | 66.4194 |  | 110.5274
02/13 13:00:00 | 23.3131 | 25.3022 | 24.5524 | 24.7716 | 24.7356 | 25.0798 | 22.8492 | 40.203 | 30.8195 | 36.023 | 34.4301 | 34.3215 | 36.5293 | 15.9494 | [14 empty] | 0.21515 |  | 588.2378 |  |  |  | 221.1193 |  | 402.9491 |  | 341.5339 |  | 337.5314 |  | 423.5294
02/13 14:00:00 | 23.5913 | 25.4142 | 24.708 | 24.7468 | 24.7108 | 25.1665 | 22.979 | 36.5378 | 26.6064 | 31.8752 | 30.957 | 30.7738 | 31.7373 | 3.6036 | [14 empty] | 0.37486 |  | 1084.6628 |  |  |  | 529.1294 |  | 799.2833 |  | 748.2083 |  | 738.2175 |  | 791.5019
02/13 15:00:00 | 24.1314 | 25.8624 | 25.0698 | 24.953 | 24.9406 | 25.5821 | 22.7821 | 33.2651 | 23.8292 | 28.8177 | 27.8602 | 27.6669 | 28.6105 | 3.0283 | [14 empty] | 1.8206 |  | 914.2659 |  |  |  | 432.6788 |  | 665.0968 |  | 616.6241 |  | 607.0625 |  | 654.452
02/13 16:00:00 | 24.7288 | 26.503 | 25.6711 | 25.4676 | 25.4898 | 26.1686 | 22.6971 | 30.3909 | 20.2817 | 26.012 | 25.0999 | 24.6953 | 25.3791 | 28.5446 | [14 empty] | 4.128 |  | 3.4086 |  |  |  | 68.2752 |  | 6.4141 |  | 11.8661 |  | 14.8171 |  | 10.0207
02/13 17:00:00 | 25.0598 | 26.9249 | 26.0326 | 25.7829 | 25.8205 | 26.5027 | 22.8836 | 28.298 | 18.0051 | 23.8254 | 22.7575 | 22.3043 | 22.7157 | 9.9346 | [14 empty] | 4.7359 |  | 337.2154 |  |  |  | 65.1335 |  | 192.9562 |  | 164.427 |  | 153.0106 |  | 163.3577
02/13 18:00:00 | 25.1895 | 27.0685 | 26.1599 | 25.8666 | 25.9124 | 26.6147 | 22.7937 | 26.8681 | 19.4356 | 23.3785 | 22.2413 | 22.1613 | 22.9621 | 35.3166 | [14 empty] | 5.7399 |  | 71.377 |  |  |  | 252.206 |  | 142.5201 |  | 170.9635 |  | 173.0639 |  | 152.6337
02/13 19:00:00 | 25.1092 | 26.9779 | 26.0754 | 25.7359 | 25.77 | 26.4825 | 22.6166 | 27.8255 | 22.2096 | 24.5297 | 23.2938 | 23.3039 | 25.4746 | 32.9622 | [14 empty] | 6.2134 |  | 26.3858 |  |  |  | 115.6197 |  | 71.1082 |  | 93.4787 |  | 93.2843 |  | 56.0654
02/13 20:00:00 | 24.6419 | 26.419 | 25.5803 | 25.1624 | 25.189 | 25.9116 | 22.5093 | 27.1199 | 21.6109 | 23.9764 | 22.7827 | 22.7405 | 24.5888 | 31.138 | [14 empty] | 4.5478 |  | 16.1457 |  |  |  | 90.7661 |  | 51.2887 |  | 69.8112 |  | 70.5196 |  | 42.8929
02/13 21:00:00 | 24.1216 | 25.8703 | 25.0875 | 24.5473 | 24.5598 | 25.3451 | 22.2769 | 21.1277 | 15.9135 | 18.0483 | 17.4088 | 17.3108 | 18.6112 | 8.7351 | [14 empty] | 3.4027 |  | 153.576 |  |  |  | 51.5288 |  | 86.7347 |  | 75.2321 |  | 73.5422 |  | 97.5364
02/13 22:00:00 | 23.7423 | 25.4564 | 24.6784 | 24.0691 | 23.9729 | 24.8234 | 21.8307 | 20.4343 | 15.4677 | 17.4654 | 16.9572 | 16.8855 | 18.1066 | 19.4016 | [14 empty] | 3.6543 |  | 1.0665 |  |  |  | 15.4756 |  | 3.749 |  | 5.9752 |  | 6.3308 |  | 1.6771
02/13 23:00:00 | 23.4046 | 25.0104 | 24.3624 | 23.6113 | 23.4165 | 24.3083 | 21.5709 | 20.6154 | 15.2851 | 17.3928 | 17.1802 | 17.1359 | 18.3156 | 20.2084 | [14 empty] | 3.3627 |  | 0.16565 |  |  |  | 24.2389 |  | 7.9276 |  | 9.1699 |  | 9.4403 |  | 3.5827
02/13 24:00:00 | 23.0154 | 24.5578 | 24.0011 | 23.1433 | 22.8513 | 23.7778 | 21.374 | 20.328 | 15.1 | 17.1956 | 17.1454 | 17.1422 | 18.2712 | 21.9699 | [14 empty] | 2.6943 |  | 2.6956 |  |  |  | 47.1947 |  | 22.7941 |  | 23.2758 |  | 23.3064 |  | 13.6801
02/14 01:00:00 | 22.6201 | 24.107 | 23.5496 | 22.6554 | 22.362 | 23.3139 | 21.1843 | 19.9169 | 14.814 | 16.8175 | 16.9001 | 16.9046 | 17.97 | 22.3793 | [14 empty] | 2.0615 |  | 6.0632 |  |  |  | 57.233 |  | 30.933 |  | 30.021 |  | 29.972 |  | 19.4416
02/14 02:00:00 | 22.292 | 23.6908 | 23.2272 | 22.2095 | 21.9161 | 22.8875 | 21.0287 | 18.196 | 14.2359 | 15.7961 | 15.4482 | 15.4907 | 16.4522 | 23.9334 | [14 empty] | 1.5959 |  | 32.9181 |  |  |  | 94.0416 |  | 66.2171 |  | 71.9991 |  | 71.2799 |  | 55.9689
02/14 03:00:00 | 21.9798 | 23.3753 | 22.9435 | 21.879 | 21.5796 | 22.4911 | 20.916 | 17.5561 | 13.757 | 15.2091 | 14.9458 | 14.9797 | 15.8805 | 24.3511 | [14 empty] | 1.1316 |  | 46.1713 |  |  |  | 112.2355 |  | 83.5762 |  | 88.46 |  | 87.8236 |  | 71.7512
02/14 04:00:00 | 21.6755 | 23.0892 | 22.6645 | 21.5715 | 21.2619 | 22.1755 | 20.7906 | 17.4486 | 13.4315 | 14.9681 | 14.9207 | 14.9448 | 15.8414 | 25.188 | [14 empty] | 0.78307 |  | 59.8992 |  |  |  | 138.216 |  | 104.4462 |  | 105.4182 |  | 104.9238 |  | 87.3598
02/14 05:00:00 | 21.376 | 22.7975 | 22.3825 | 21.2591 | 20.9365 | 21.8743 | 20.7036 | 14.1103 | 12.9615 | 14.3123 | 14.0774 | 14.1223 | 14.9517 | 26.1807 | [14 empty] | 0.45213 |  | 145.6952 |  |  |  | 174.7485 |  | 140.8612 |  | 146.4903 |  | 145.4056 |  | 126.0911
02/14 06:00:00 | 21.1345 | 22.5076 | 22.111 | 20.9501 | 20.614 | 21.5752 | 20.6402 | 15.2905 | 12.4119 | 13.3352 | 12.8483 | 12.8997 | 13.6267 | 26.1118 | [14 empty] | 0.24434 |  | 117.0994 |  |  |  | 187.6867 |  | 163.241 |  | 175.9212 |  | 174.5598 |  | 155.8771
02/14 07:00:00 | 20.9088 | 22.2133 | 21.8336 | 20.6382 | 20.2867 | 21.2673 | 20.6071 | 14.552 | 11.934 | 10.9593 | 12.4122 | 32.6907 | 13.1413 | 26.5838 | [14 empty] | 0.091015 |  | 144.7655 |  |  |  | 214.6183 |  | 244.1253 |  | 200.8339 |  | 37.2939 |  | 180.7026
02/14 08:00:00 | 20.6095 | 21.9132 | 21.608 | 20.3338 | 20.1313 | 20.9613 | 20.9902 | 15.0632 | 16.3988 | 14.0264 | 39.4991 | 63.6117 | 41.2046 | 81.7312 | [14 empty] | 0.1449 |  | 4444.6106 |  |  |  | 4268.3187 |  | 4583.9348 |  | 1783.5427 |  | 328.3165 |  | 1642.4001
02/14 09:00:00 | 20.3915 | 21.6455 | 21.4613 | 20.2335 | 20.9589 | 20.8692 | 22.2579 | 38.8237 | 37.7557 | 38.4784 | 59.8996 | 59.2748 | 60.681 | 41.4518 | [14 empty] | 3.4834 |  | 6.907 |  |  |  | 13.6613 |  | 8.8412 |  | 340.3215 |  | 317.6602 |  | 369.7633
02/14 10:00:00 | 20.5529 | 21.705 | 21.6275 | 21.2408 | 22.3933 | 21.9657 | 22.6922 | 49.5892 | 42.5969 | 49.6093 | 55.2589 | 45.2896 | 45.3986 | 26.6048 | [14 empty] | 4.5763 |  | 528.2801 |  |  |  | 255.7458 |  | 529.2033 |  | 821.0559 |  | 349.1221 |  | 353.2051
02/14 11:00:00 | 21.4709 | 22.9712 | 22.6065 | 23.3195 | 23.9016 | 23.9769 | 22.9183 | 50.869 | 30.9862 | 40.3661 | 44.3444 | 39.5989 | 37.7394 | 7.8667 | [14 empty] | 2.0949 |  | 1849.1923 |  |  |  | 534.5119 |  | 1056.2099 |  | 1330.6244 |  | 1006.928 |  | 892.3774
02/14 12:00:00 | 22.7377 | 24.3896 | 24.1491 | 24.7647 | 24.763 | 25.073 | 23.0922 | 40.4245 | 25.0623 | 32.3561 | 35.9042 | 33.6995 | 31.179 | 3.3926 | [14 empty] | 0.12564 |  | 1371.3573 |  |  |  | 469.5768 |  | 838.8854 |  | 1057.006 |  | 918.5048 |  | 772.081
02/14 13:00:00 | 24.3839 | 25.6277 | 25.4291 | 25.5641 | 25.5197 | 25.8637 | 23.1193 | 36.5328 | 23.211 | 29.6287 | 33.6608 | 31.4247 | 29.3032 | 3.1017 | [14 empty] | 1.5993 |  | 1117.6411 |  |  |  | 404.3834 |  | 703.681 |  | 933.8587 |  | 802.1934 |  | 686.5189
02/14 14:00:00 | 24.9064 | 26.0572 | 25.7693 | 25.788 | 25.7625 | 26.0581 | 23.1193 | 34.9432 | 21.0203 | 27.5755 | 31.4187 | 29.3641 | 27.268 | 2.983 | [14 empty] | 3.194 |  | 1021.4556 |  |  |  | 325.3415 |  | 604.7912 |  | 808.5853 |  | 695.9605 |  | 589.7603
02/14 15:00:00 | 25.0891 | 26.2657 | 26.0234 | 26.002 | 25.9772 | 26.2541 | 23.1458 | 31.5109 | 18.7768 | 24.4828 | 27.9006 | 26.1773 | 23.8747 | 2.8828 | [14 empty] | 3.7763 |  | 819.5644 |  |  |  | 252.6165 |  | 466.5593 |  | 625.8874 |  | 542.6316 |  | 440.658
02/14 16:00:00 | 25.6151 | 26.8103 | 26.5953 | 26.5025 | 26.4792 | 26.78 | 23.2103 | 27.6353 | 15.1815 | 20.8642 | 24.057 | 22.5947 | 19.7856 | 2.8636 | [14 empty] | 5.7832 |  | 613.6414 |  |  |  | 151.7319 |  | 324.0246 |  | 449.1629 |  | 389.3167 |  | 286.356
02/14 17:00:00 | 26.0394 | 27.3148 | 27.0434 | 26.892 | 26.8678 | 27.1978 | 23.1733 | 24.8154 | 12.6831 | 17.8515 | 21.0304 | 19.9531 | 16.6384 | 2.8701 | [14 empty] | 8.2145 |  | 481.5986 |  |  |  | 96.2945 |  | 224.4425 |  | 329.7965 |  | 291.8296 |  | 189.5676
02/14 18:00:00 | 26.2321 | 27.5772 | 27.2319 | 27.0451 | 27.0175 | 27.3725 | 22.8625 | 24.9152 | 15.0875 | 19.5918 | 22.442 | 21.0176 | 19.0219 | 34.7654 | [14 empty] | 11.354 |  | 97.0257 |  |  |  | 387.2181 |  | 230.2355 |  | 151.8645 |  | 189.0001 |  | 247.8568
02/14 19:00:00 | 26.2261 | 27.5406 | 27.2042 | 26.981 | 26.9354 | 27.3054 | 22.7378 | 25.1211 | 17.4527 | 21.445 | 23.9079 | 22.6741 | 21.242 | 8.5429 | [14 empty] | 12.168 |  | 274.8366 |  |  |  | 79.3847 |  | 166.4661 |  | 236.0841 |  | 199.6917 |  | 161.2691
02/14 20:00:00 | 25.7877 | 26.9889 | 26.7703 | 26.4948 | 26.4471 | 26.7573 | 22.4387 | 25.0001 | 17.0378 | 21.4854 | 23.7229 | 22.3194 | 21.1277 | 17.0228 | [14 empty] | 11.2155 |  | 63.6381 |  |  |  | 0.00022504 |  | 19.9144 |  | 44.892 |  | 28.0536 |  | 16.8503
02/14 21:00:00 | 25.3314 | 26.4974 | 26.3687 | 26.0616 | 26.0019 | 26.2977 | 22.114 | 19.7031 | 12.6462 | 16.1497 | 17.9731 | 16.8085 | 16.0757 | 11.4126 | [14 empty] | 10.3514 |  | 68.7318 |  |  |  | 1.5217 |  | 22.4402 |  | 43.0409 |  | 29.1154 |  | 21.7444
02/14 22:00:00 | 25.0142 | 26.1378 | 26.0357 | 25.6887 | 25.5749 | 25.9183 | 21.804 | 18.8672 | 12.3434 | 15.512 | 17.1554 | 16.144 | 15.3992 | 17.4036 | [14 empty] | 10.3056 |  | 2.1422 |  |  |  | 25.6061 |  | 3.5784 |  | 0.061599 |  | 1.5867 |  | 4.0175
02/14 23:00:00 | 24.6866 | 25.7647 | 25.7085 | 25.2721 | 25.0687 | 25.5206 | 21.6067 | 18.3796 | 12.115 | 15.1495 | 16.8412 | 15.8548 | 15.1302 | 19.3598 | [14 empty] | 9.4861 |  | 0.96074 |  |  |  | 52.4864 |  | 17.7268 |  | 6.3431 |  | 12.2848 |  | 17.8895
02/14 24:00:00 | 24.3035 | 25.3852 | 25.3837 | 24.8652 | 24.5838 | 25.1187 | 21.4691 | 17.6018 | 11.7898 | 14.5948 | 16.1981 | 15.3226 | 14.5777 | 19.1134 | [14 empty] | 8.0337 |  | 2.2848 |  |  |  | 53.6342 |  | 20.4178 |  | 8.4989 |  | 14.3698 |  | 20.5727
02/15 01:00:00 | 24.0276 | 25.0879 | 25.1348 | 24.5631 | 24.2061 | 24.8088 | 21.4082 | 17.1727 | 11.4877 | 14.2319 | 15.8492 | 15.0116 | 14.3089 | 19.5718 | [14 empty] | 6.8615 |  | 5.7556 |  |  |  | 65.3526 |  | 28.5136 |  | 13.8571 |  | 20.7947 |  | 27.6976
02/15 02:00:00 | 23.8076 | 24.8082 | 24.9329 | 24.2793 | 23.8808 | 24.5146 | 21.3754 | 13.2444 | 11.0113 | 11.1661 | 14.8022 | 14.0456 | 13.3451 | 19.308 | [14 empty] | 5.916 |  | 36.7673 |  |  |  | 68.8352 |  | 66.2912 |  | 20.3023 |  | 27.6928 |  | 35.557
02/15 03:00:00 | 23.628 | 24.5439 | 24.7688 | 24.0252 | 23.6469 | 24.2509 | 21.4601 | 13.8897 | 10.811 | 11.5473 | 14.9719 | 14.2185 | 13.5896 | 18.1322 | [14 empty] | 4.6995 |  | 17.9987 |  |  |  | 53.5998 |  | 43.3603 |  | 9.9871 |  | 15.3169 |  | 20.6345
02/15 04:00:00 | 23.4912 | 24.319 | 24.6412 | 23.7962 | 23.4227 | 24.0154 | 21.4134 | 13.7066 | 10.5917 | 11.4203 | 14.6726 | 13.9563 | 13.3468 | 19.7074 | [14 empty] | 4.3174 |  | 36.0106 |  |  |  | 83.0963 |  | 68.6768 |  | 25.3499 |  | 33.0755 |  | 40.4576
02/15 05:00:00 | 23.353 | 24.0988 | 24.5094 | 23.5683 | 23.1935 | 23.7826 | 21.3532 | 13.3404 | 10.3364 | 11.1565 | 14.2126 | 13.539 | 12.9405 | 19.5789 | [14 empty] | 3.9993 |  | 38.9191 |  |  |  | 85.4243 |  | 70.9382 |  | 28.7976 |  | 36.4813 |  | 44.0689
02/15 06:00:00 | 23.202 | 23.8711 | 24.3632 | 23.3274 | 22.9474 | 23.5313 | 21.294 | 13.1871 | 10.1265 | 13.0088 | 13.9487 | 13.3098 | 12.7274 | 20.4617 | [14 empty] | 3.6406 |  | 52.9199 |  |  |  | 106.8167 |  | 55.5459 |  | 42.4185 |  | 51.1497 |  | 59.8196
02/15 07:00:00 | 23.038 | 23.631 | 24.1636 | 23.0691 | 22.681 | 23.2634 | 21.2406 | 12.8476 | 9.9153 | 12.332 | 13.5371 | 12.9384 | 12.4151 | 21.0985 | [14 empty] | 3.2307 |  | 68.0784 |  |  |  | 125.0639 |  | 76.852 |  | 57.1757 |  | 66.5882 |  | 75.4029
02/15 08:00:00 | 22.8647 | 23.3824 | 23.8787 | 22.7996 | 22.4015 | 22.9936 | 21.4661 | 17.6603 | 12.5869 | 14.9477 | 15.9924 | 15.4617 | 14.5656 | 74.2792 | [14 empty] | 1.956 |  | 3205.6934 |  |  |  | 3805.9341 |  | 3520.2248 |  | 3397.3451 |  | 3459.4961 |  | 3565.7085
02/15 09:00:00 | 22.6461 | 23.1367 | 23.6119 | 22.5294 | 22.1082 | 22.7143 | 22.3808 | 17.8862 | 12.2161 | 14.5446 | 17.5944 | 30.0543 | 14.1459 | 24.2567 | [14 empty] | 0.070375 |  | 40.5835 |  |  |  | 144.976 |  | 94.3239 |  | 44.3856 |  | 33.6127 |  | 102.2288
02/15 10:00:00 | 22.3931 | 22.9282 | 23.3971 | 22.2967 | 21.9511 | 22.4758 | 22.5187 | 27.8693 | 11.5474 | 13.5038 | 31.8577 | 43.4547 | 14.157 | 23.0402 | [14 empty] | 0.015781 |  | 23.3209 |  |  |  | 132.0835 |  | 90.9424 |  | 77.7484 |  | 416.7522 |  | 78.9108
02/15 11:00:00 | 22.4672 | 22.9222 | 23.3939 | 22.4052 | 22.5704 | 22.4382 | 22.5265 | 35.0541 | 10.5274 | 12.2368 | 41.2904 | 42.025 | 27.5249 | 17.7697 | [14 empty] | 0.0035182 |  | 298.7497 |  |  |  | 52.4517 |  | 30.613 |  | 553.2235 |  | 588.3163 |  | 95.1634
02/15 12:00:00 | 22.8625 | 23.0357 | 23.502 | 23.1006 | 23.7148 | 22.6386 | 22.6278 | 29.9369 | 9.382 | 11.0368 | 31.0125 | 32.5157 | 41.4571 | 17.2627 | [14 empty] | 0.055117 |  | 160.6362 |  |  |  | 62.1053 |  | 38.7616 |  | 189.0563 |  | 232.654 |  | 585.3713
02/15 13:00:00 | 23.4281 | 23.227 | 23.6414 | 24.1269 | 24.6244 | 23.5881 | 22.5196 | 26.8367 | 8.5619 | 10.4112 | 26.8884 | 28.5939 | 29.5646 | 26.2878 | [14 empty] | 0.82541 |  | 0.30133 |  |  |  | 314.2079 |  | 252.0659 |  | 0.3607 |  | 5.3182 |  | 10.7376
02/15 14:00:00 | 23.5692 | 23.0656 | 23.4321 | 24.3892 | 24.7454 | 24.4353 | 22.4704 | 26.255 | 8.5162 | 10.4483 | 26.3774 | 28.0736 | 25.8353 | 28.0239 | [14 empty] | 1.2075 |  | 3.1289 |  |  |  | 380.5473 |  | 308.9015 |  | 2.7108 |  | 0.0024694 |  | 4.7898
02/15 15:00:00 | 23.5729 | 22.8988 | 23.2618 | 24.3273 | 24.687 | 24.6551 | 22.3774 | 24.5628 | 8.351 | 10.0704 | 24.4962 | 26.1555 | 24.3887 | 28.5882 | [14 empty] | 1.4291 |  | 16.204 |  |  |  | 409.5417 |  | 342.9086 |  | 16.7445 |  | 5.9181 |  | 17.636
02/15 16:00:00 | 23.7534 | 23.0173 | 23.3843 | 24.4391 | 24.7789 | 24.8248 | 22.278 | 23.8923 | 8.3002 | 9.9965 | 23.7951 | 25.2524 | 23.7885 | 29.4498 | [14 empty] | 2.1766 |  | 30.8861 |  |  |  | 447.3065 |  | 378.4315 |  | 31.9758 |  | 17.6182 |  | 32.0512
02/15 17:00:00 | 23.8108 | 23.072 | 23.4202 | 24.4352 | 24.7863 | 24.8499 | 22.1897 | 23.0939 | 8.2933 | 9.9674 | 22.8275 | 24.1552 | 22.8493 | 29.3117 | [14 empty] | 2.6281 |  | 38.6605 |  |  |  | 441.7713 |  | 374.2008 |  | 42.0446 |  | 26.589 |  | 41.7627
02/15 18:00:00 | 23.6207 | 22.8789 | 23.197 | 24.1893 | 24.5403 | 24.6193 | 22.0629 | 21.025 | 8.0596 | 9.2852 | 20.7723 | 22.0008 | 20.8069 | 31.21 | [14 empty] | 2.4268 |  | 103.7356 |  |  |  | 535.9416 |  | 480.698 |  | 108.9472 |  | 84.8097 |  | 108.2247
02/15 19:00:00 | 23.3469 | 22.6077 | 22.8889 | 23.8129 | 24.155 | 24.2543 | 22.0464 | 20.9111 | 13.7345 | 9.4122 | 20.4817 | 21.6358 | 20.5127 | 33.0063 | [14 empty] | 1.6912 |  | 146.2932 |  |  |  | 371.4002 |  | 556.679 |  | 156.8653 |  | 129.2887 |  | 156.09
02/15 20:00:00 | 22.8435 | 22.1035 | 22.3425 | 23.2194 | 23.5514 | 23.6742 | 22.0081 | 20.1378 | 32.603 | 15.9469 | 19.6611 | 20.7625 | 19.6882 | 32.1693 | [14 empty] | 0.69791 |  | 144.7559 |  |  |  | 0.18812 |  | 263.1638 |  | 156.4544 |  | 130.1144 |  | 155.7766
02/15 21:00:00 | 22.2075 | 21.7938 | 21.6858 | 22.5711 | 22.8899 | 23.0323 | 21.8178 | 16.2744 | 20.5246 | 13.9941 | 15.7037 | 16.4523 | 15.7325 | 11.2356 | [14 empty] | 0.15188 |  | 25.3896 |  |  |  | 86.2853 |  | 7.6097 |  | 19.9641 |  | 27.214 |  | 20.2228
02/15 22:00:00 | 21.753 | 21.73 | 21.385 | 22.0899 | 22.2858 | 22.4423 | 21.3107 | 15.7426 | 15.8745 | 10.6969 | 15.2516 | 15.978 | 15.2939 | 21.5794 | [14 empty] | 0.19558 |  | 34.0688 |  |  |  | 32.5463 |  | 118.4293 |  | 40.0411 |  | 31.3764 |  | 39.5085
02/15 23:00:00 | 21.3471 | 21.5501 | 21.0388 | 21.5858 | 21.6537 | 21.879 | 21.0128 | 15.9473 | 16.3479 | 11.3877 | 15.4527 | 16.1857 | 15.4785 | 23.3466 | [14 empty] | 0.11175 |  | 54.7492 |  |  |  | 48.9819 |  | 143.0156 |  | 62.3137 |  | 51.2791 |  | 61.9076
02/15 24:00:00 | 20.89 | 21.313 | 20.6331 | 20.9944 | 21.0561 | 21.3363 | 20.8232 | 15.1015 | 15.9924 | 11.0641 | 14.7084 | 15.4388 | 14.7349 | 26.1225 | [14 empty] | 0.0044645 |  | 121.463 |  |  |  | 102.618 |  | 226.7569 |  | 130.2818 |  | 114.1419 |  | 129.6766
02/16 01:00:00 | 20.4723 | 21.0645 | 20.2674 | 20.5725 | 20.5414 | 20.9444 | 20.6277 | 28.7147 | 15.3623 | 26.8524 | 13.8457 | 14.5364 | 13.8676 | 27.2517 | [14 empty] | 0.024154 |  | 2.1403 |  |  |  | 141.3569 |  | 0.15941 |  | 179.7188 |  | 161.6771 |  | 179.1331
02/16 02:00:00 | 20.3043 | 20.8369 | 20.1496 | 20.2376 | 20.1122 | 20.6271 | 20.4598 | 41.0638 | 14.7994 | 39.6255 | 31.4972 | 33.1738 | 13.3498 | 27.996 | [14 empty] | 0.024176 |  | 170.7662 |  |  |  | 174.1511 |  | 135.2459 |  | 12.2586 |  | 26.8096 |  | 214.5121
02/16 03:00:00 | 20.536 | 20.6033 | 20.4485 | 20.0701 | 19.9389 | 20.3101 | 20.4346 | 35.4388 | 14.2846 | 40.4519 | 43.9219 | 46.3517 | 31.765 | 26.6022 | [14 empty] | 0.010268 |  | 78.0845 |  |  |  | 151.7238 |  | 191.8125 |  | 299.971 |  | 390.0402 |  | 26.654
02/16 04:00:00 | 20.814 | 20.3602 | 20.8553 | 20.2785 | 20.1865 | 20.1475 | 20.3241 | 25.3607 | 11.9475 | 35.5996 | 44.4084 | 44.9864 | 44.7559 | 29.1462 | [14 empty] | 0.24001 |  | 14.3295 |  |  |  | 295.7944 |  | 41.6467 |  | 232.936 |  | 250.913 |  | 243.6633
02/16 05:00:00 | 20.8393 | 20.1575 | 21.2106 | 20.5994 | 20.5393 | 20.3667 | 20.2213 | 24.9583 | 29.7519 | 32.1672 | 38.2837 | 38.1964 | 44.3639 | 29.2944 | [14 empty] | 0.38192 |  | 18.8015 |  |  |  | 0.20926 |  | 8.2529 |  | 80.8074 |  | 79.2444 |  | 227.0892
02/16 06:00:00 | 20.7844 | 20.123 | 21.3846 | 20.8707 | 20.7925 | 20.6957 | 20.125 | 23.4133 | 38.4415 | 24.7536 | 33.8048 | 33.601 | 37.2892 | 29.9407 | [14 empty] | 0.43484 |  | 42.6067 |  |  |  | 72.2635 |  | 26.906 |  | 14.9315 |  | 13.3975 |  | 54.001
02/16 07:00:00 | 20.7058 | 20.2851 | 21.3802 | 20.9745 | 20.8722 | 20.986 | 20.0974 | 27.5621 | 38.23 | 29.7162 | 31.8714 | 31.7951 | 32.8127 | 29.5088 | [14 empty] | 0.37008 |  | 3.7897 |  |  |  | 76.0596 |  | 0.043002 |  | 5.5819 |  | 5.2272 |  | 10.9155
02/16 08:00:00 | 20.6564 | 20.5609 | 21.388 | 20.9838 | 20.8597 | 21.1122 | 20.3673 | 42.6942 | 53.7481 | 30.3305 | 54.934 | 57.6909 | 56.4662 | 79.9072 | [14 empty] | 0.083534 |  | 1384.8083 |  |  |  | 684.2997 |  | 2457.8466 |  | 623.6585 |  | 493.5627 |  | 549.4787
02/16 09:00:00 | 20.6524 | 21.5464 | 21.3281 | 21.2638 | 21.3029 | 21.6831 | 21.4271 | 49.8259 | 49.6501 | 46.1087 | 55.8906 | 56.99 | 55.4939 | 68.3986 | [14 empty] | 0.60019 |  | 344.9443 |  |  |  | 351.5074 |  | 496.8394 |  | 156.4502 |  | 130.1554 |  | 166.5313
02/16 10:00:00 | 21.0404 | 22.8343 | 21.6154 | 22.3217 | 22.2969 | 22.7481 | 22.2975 | 51.5449 | 42.6032 | 51.2165 | 48.7387 | 49.1135 | 46.8673 | 36.6788 | [14 empty] | 1.5803 |  | 221.0007 |  |  |  | 35.0981 |  | 211.3435 |  | 145.4405 |  | 154.6216 |  | 103.8058
02/16 11:00:00 | 21.7441 | 23.9255 | 22.5887 | 23.5268 | 23.3633 | 23.7912 | 22.3212 | 47.6911 | 39.0535 | 45.3233 | 43.8006 | 43.8664 | 42.4345 | 36.1573 | [14 empty] | 0.33314 |  | 133.028 |  |  |  | 8.3881 |  | 84.0159 |  | 58.4197 |  | 59.4294 |  | 39.4031
02/16 12:00:00 | 22.3021 | 24.4665 | 23.7282 | 24.1028 | 23.8826 | 24.2659 | 22.3551 | 43.9943 | 36.611 | 40.5934 | 40.3943 | 40.2125 | 39.4893 | 36.0276 | [14 empty] | 0.0028087 |  | 63.4686 |  |  |  | 0.3404 |  | 20.8466 |  | 19.0685 |  | 17.5134 |  | 11.9831
02/16 13:00:00 | 22.6377 | 24.7196 | 24.1572 | 24.2672 | 24.1033 | 24.4776 | 22.3714 | 42.5592 | 34.3116 | 37.1437 | 36.9453 | 36.8308 | 36.1763 | 32.7283 | [14 empty] | 0.07092 |  | 96.6468 |  |  |  | 2.5069 |  | 19.4963 |  | 17.7832 |  | 16.8307 |  | 11.8891
02/16 14:00:00 | 22.7093 | 24.7414 | 24.1202 | 24.1638 | 24.0582 | 24.4417 | 22.3266 | 38.6084 | 31.5102 | 34.0616 | 33.5907 | 33.5143 | 32.8134 | 34.415 | [14 empty] | 0.14646 |  | 17.5846 |  |  |  | 8.4384 |  | 0.12489 |  | 0.67956 |  | 0.81139 |  | 2.5654
02/16 15:00:00 | 22.8242 | 24.8255 | 24.1089 | 24.1087 | 24.0585 | 24.457 | 22.2913 | 36.2406 | 29.4801 | 32.1064 | 31.7916 | 31.7325 | 31.049 | 32.1777 | [14 empty] | 0.28391 |  | 16.5068 |  |  |  | 7.277 |  | 0.0050821 |  | 0.14909 |  | 0.19824 |  | 1.2741
02/16 16:00:00 | 23.0509 | 25.0962 | 24.2806 | 24.2223 | 24.2104 | 24.6217 | 22.4241 | 29.6 | 28.1618 | 26.2048 | 30.7657 | 30.6759 | 30.0576 | 31.7254 | [14 empty] | 0.3928 |  | 4.5174 |  |  |  | 12.6995 |  | 30.4771 |  | 0.92111 |  | 1.1015 |  | 2.7816
02/16 17:00:00 | 23.1221 | 25.2612 | 24.3419 | 24.2824 | 24.2977 | 24.7231 | 22.481 | 33.7167 | 26.5985 | 29.6999 | 28.5385 | 28.4758 | 27.8858 | 31.3089 | [14 empty] | 0.411 |  | 5.7978 |  |  |  | 22.1877 |  | 2.5889 |  | 7.6751 |  | 8.0263 |  | 11.7173
02/16 18:00:00 | 23.0944 | 25.2407 | 24.2873 | 24.1678 | 24.21 | 24.6506 | 22.1954 | 31.0672 | 25.0117 | 27.2691 | 26.6293 | 26.5502 | 25.9916 | 35.4114 | [14 empty] | 0.80808 |  | 18.8718 |  |  |  | 108.154 |  | 66.2973 |  | 77.124 |  | 78.5211 |  | 88.7323
02/16 19:00:00 | 22.9697 | 25.0661 | 24.1283 | 23.8981 | 23.9657 | 24.4173 | 22.0918 | 30.1476 | 24.0855 | 26.3457 | 25.8361 | 25.6941 | 25.2066 | 35.3489 | [14 empty] | 0.7707 |  | 27.0529 |  |  |  | 126.8641 |  | 81.0575 |  | 90.4927 |  | 93.2144 |  | 102.8662
02/16 20:00:00 | 22.5792 | 24.6087 | 23.6933 | 23.3441 | 23.3841 | 23.8459 | 22.0438 | 29.6196 | 23.1579 | 25.2613 | 24.6836 | 24.5985 | 24.1374 | 49.5676 | [14 empty] | 0.28672 |  | 397.9206 |  |  |  | 697.4692 |  | 590.7945 |  | 619.211 |  | 623.4537 |  | 646.6946
02/16 21:00:00 | 22.0751 | 24.0748 | 23.1439 | 22.7424 | 22.7939 | 23.2614 | 22.03 | 24.3308 | 17.0712 | 19.1847 | 19.1998 | 19.0368 | 18.7805 | 4.923 | [14 empty] | 0.0020355 |  | 376.6643 |  |  |  | 147.5799 |  | 203.3969 |  | 203.8268 |  | 199.1991 |  | 192.0309
02/16 22:00:00 | 21.7533 | 23.548 | 22.734 | 22.1836 | 22.2069 | 22.6873 | 21.4876 | 21.3165 | 16.414 | 17.957 | 17.5773 | 17.5076 | 17.245 | 21.6671 | [14 empty] | 0.070586 |  | 0.12295 |  |  |  | 27.595 |  | 13.7652 |  | 16.7268 |  | 17.3015 |  | 19.5549
02/16 23:00:00 | 21.442 | 23.0069 | 22.3789 | 21.6372 | 21.5585 | 22.072 | 21.0706 | 21.7944 | 16.1384 | 17.9525 | 17.9812 | 17.9077 | 17.6443 | 25.0272 | [14 empty] | 0.13794 |  | 10.4509 |  |  |  | 79.0117 |  | 50.052 |  | 49.6465 |  | 50.6882 |  | 54.5079
02/16 24:00:00 | 21.0706 | 22.3911 | 21.9777 | 21.0135 | 20.857 | 21.4918 | 20.7835 | 21.1147 | 15.9013 | 17.5121 | 17.6304 | 17.5756 | 17.3087 | 26.5494 | [14 empty] | 0.082441 |  | 29.5354 |  |  |  | 113.38 |  | 81.6714 |  | 79.5481 |  | 80.5277 |  | 85.3891
02/17 01:00:00 | 20.7081 | 21.9075 | 21.5913 | 20.5322 | 20.3125 | 21.0267 | 20.5871 | 20.794 | 15.5787 | 17.2204 | 17.4982 | 37.8223 | 17.1847 | 28.2944 | [14 empty] | 0.014636 |  | 56.257 |  |  |  | 161.69 |  | 122.6332 |  | 116.5581 |  | 90.7805 |  | 123.426
02/17 02:00:00 | 20.4099 | 21.4912 | 21.2744 | 20.1097 | 20.0737 | 20.6106 | 20.461 | 32.0578 | 15.1344 | 16.6115 | 33.1399 | 46.7164 | 16.4868 | 28.7684 | [14 empty] | 0.002606 |  | 10.8202 |  |  |  | 185.8849 |  | 147.7904 |  | 19.1107 |  | 322.1326 |  | 150.8361
02/17 03:00:00 | 20.251 | 21.1714 | 20.964 | 19.9271 | 20.349 | 20.29 | 20.4632 | 33.4102 | 14.5969 | 13.2963 | 44.1021 | 44.6718 | 32.9978 | 27.177 | [14 empty] | 0.045016 |  | 38.8538 |  |  |  | 158.2584 |  | 192.6738 |  | 286.4606 |  | 306.0693 |  | 33.8818
02/17 04:00:00 | 20.2814 | 20.8959 | 20.721 | 20.1361 | 20.6954 | 20.1559 | 20.3947 | 36.1534 | 14.0428 | 13.0771 | 44.1885 | 38.4173 | 44.4128 | 29.9849 | [14 empty] | 0.012854 |  | 38.0499 |  |  |  | 254.1512 |  | 285.8723 |  | 201.7421 |  | 71.1049 |  | 208.1655
02/17 05:00:00 | 20.3642 | 20.6284 | 20.5481 | 20.4517 | 20.9145 | 20.3824 | 20.3739 | 37.267 | 13.5374 | 12.7389 | 44.1355 | 34.6873 | 44.2511 | 28.5868 | [14 empty] | 9.3421e-05 |  | 75.3463 |  |  |  | 226.4865 |  | 251.1579 |  | 241.7621 |  | 37.2161 |  | 245.3693
02/17 06:00:00 | 20.4509 | 20.3581 | 20.3698 | 20.7557 | 20.9689 | 20.7039 | 20.4186 | 37.5337 | 28.6844 | 12.3541 | 39.8016 | 33.4134 | 38.2203 | 28.7636 | [14 empty] | 0.0010432 |  | 76.9153 |  |  |  | 0.0062734 |  | 269.2701 |  | 121.8385 |  | 21.6205 |  | 89.4295
02/17 07:00:00 | 20.5377 | 20.2123 | 20.1883 | 20.9907 | 20.9343 | 20.9819 | 20.3624 | 39.2423 | 38.9247 | 20.6754 | 35.9314 | 31.2458 | 33.8734 | 30.3264 | [14 empty] | 0.030743 |  | 79.493 |  |  |  | 73.9296 |  | 93.1424 |  | 31.4157 |  | 0.8452 |  | 12.5813
02/17 08:00:00 | 20.6476 | 20.3844 | 20.1068 | 21.0874 | 20.8416 | 21.1033 | 20.7848 | 42.0091 | 53.6354 | 49.6112 | 55.0979 | 56.0125 | 55.2499 | 81.4075 | [14 empty] | 0.018826 |  | 1552.2373 |  |  |  | 771.2916 |  | 1011.002 |  | 692.194 |  | 644.9077 |  | 684.2213
02/17 09:00:00 | 20.7551 | 21.4238 | 20.4297 | 21.6207 | 21.2764 | 21.8131 | 22.2984 | 50.1491 | 49.0595 | 51.6166 | 55.5565 | 57.1362 | 48.6377 | 37.0783 | [14 empty] | 2.3818 |  | 170.8476 |  |  |  | 143.5492 |  | 211.3641 |  | 341.446 |  | 402.3216 |  | 133.62
02/17 10:00:00 | 21.2357 | 22.9008 | 21.357 | 22.6946 | 22.2966 | 22.8846 | 22.9306 | 47.862 | 37.2409 | 47.0886 | 43.0818 | 41.8064 | 37.4446 | 4.6261 | [14 empty] | 2.8728 |  | 1869.3442 |  |  |  | 1063.73 |  | 1803.0641 |  | 1478.8422 |  | 1382.3803 |  | 1077.0552
02/17 11:00:00 | 22.5445 | 24.6348 | 23.3812 | 24.1809 | 24.0229 | 24.3123 | 22.914 | 41.9474 | 30.2062 | 39.0074 | 37.7806 | 36.206 | 33.7856 | 3.1834 | [14 empty] | 0.13651 |  | 1502.65 |  |  |  | 730.2319 |  | 1283.361 |  | 1196.9656 |  | 1090.4921 |  | 936.4983
02/17 12:00:00 | 23.996 | 25.8646 | 25.0021 | 25.18 | 25.1076 | 25.3075 | 22.8698 | 38.5191 | 24.8714 | 34.0205 | 34.3334 | 33.187 | 30.648 | 2.9988 | [14 empty] | 1.2683 |  | 1261.6928 |  |  |  | 478.4112 |  | 962.349 |  | 981.8563 |  | 911.329 |  | 764.4793
02/17 13:00:00 | 24.7803 | 26.5346 | 25.8452 | 25.784 | 25.6747 | 25.8957 | 22.9495 | 35.8128 | 24.5574 | 31.9768 | 31.9364 | 30.9359 | 28.3968 | 2.8492 | [14 empty] | 3.352 |  | 1086.5951 |  |  |  | 471.2435 |  | 848.4167 |  | 846.0629 |  | 788.8643 |  | 652.6765
02/17 14:00:00 | 24.987 | 26.7122 | 26.0147 | 25.9533 | 25.8694 | 26.1103 | 23.0823 | 31.7631 | 17.9438 | 26.0837 | 27.4661 | 26.6994 | 24.1298 | 2.7243 | [14 empty] | 3.6278 |  | 843.2521 |  |  |  | 231.6328 |  | 545.661 |  | 612.1571 |  | 574.8028 |  | 458.1944
02/17 15:00:00 | 25.3449 | 27.046 | 26.3726 | 26.2604 | 26.2046 | 26.4601 | 23.3167 | 27.9173 | 12.5435 | 20.4996 | 22.6953 | 22.3712 | 19.5514 | 2.7174 | [14 empty] | 4.1134 |  | 635.0363 |  |  |  | 96.5519 |  | 316.208 |  | 399.1145 |  | 386.2721 |  | 283.3824
02/17 16:00:00 | 25.967 | 27.6331 | 27.0354 | 26.8779 | 26.8305 | 27.1071 | 23.5207 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6131 | [14 empty] | 5.9846 |  | 6.8281 |  |  |  | 6.8281 |  | 6.8281 |  | 6.8281 |  | 6.8281 |  | 6.8281
02/17 17:00:00 | 25.9299 | 27.8385 | 27.0997 | 26.955 | 26.9589 | 27.2938 | 23.5723 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7321 | [14 empty] | 5.5583 |  | 7.4646 |  |  |  | 7.4646 |  | 7.4646 |  | 7.4646 |  | 7.4646 |  | 7.4646
02/17 18:00:00 | 25.5791 | 27.7777 | 26.8801 | 26.7318 | 26.7759 | 27.1812 | 23.3484 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8145 | [14 empty] | 4.9762 |  | 7.9213 |  |  |  | 7.9213 |  | 7.9213 |  | 7.9213 |  | 7.9213 |  | 7.9213
02/17 19:00:00 | 25.1355 | 27.4942 | 26.5788 | 26.3698 | 26.4206 | 26.8552 | 22.8845 | 0 | 0 | 0 | 0 | 0 | 0 | 18.2927 | [14 empty] | 5.0673 |  | 334.6226 |  |  |  | 334.6226 |  | 334.6226 |  | 334.6226 |  | 334.6226 |  | 334.6226
02/17 20:00:00 | 24.332 | 26.6624 | 25.883 | 25.5663 | 25.581 | 26.0035 | 22.6701 | 36.4571 | 37.8072 | 36.9026 | 38.6996 | 39.8405 | 35.4934 | 16.849 | [14 empty] | 2.7618 |  | 384.4772 |  |  |  | 439.2473 |  | 402.1493 |  | 477.45 |  | 528.6086 |  | 347.6142
02/17 21:00:00 | 24.2777 | 26.3609 | 25.8185 | 25.4297 | 25.3886 | 25.7517 | 22.43 | 24.143 | 20.5361 | 22.1794 | 21.4068 | 20.5145 | 19.1666 | 8.9221 | [14 empty] | 3.4138 |  | 231.6751 |  |  |  | 134.8843 |  | 175.754 |  | 155.8662 |  | 134.3823 |  | 104.9482
02/17 22:00:00 | 24.4143 | 26.4025 | 25.9108 | 25.4899 | 25.4236 | 25.7569 | 22.1456 | 23.4888 | 19.2212 | 21.4058 | 20.73 | 19.8028 | 18.6065 | 16.0937 | [14 empty] | 5.1473 |  | 54.6872 |  |  |  | 9.7812 |  | 28.2192 |  | 21.4958 |  | 13.758 |  | 6.3142
02/17 23:00:00 | 24.3945 | 26.3198 | 25.8641 | 25.3657 | 25.2454 | 25.5892 | 21.9524 | 23.19 | 18.9664 | 21.1561 | 20.6166 | 19.7454 | 18.5861 | 16.3169 | [14 empty] | 5.9638 |  | 47.2395 |  |  |  | 7.0196 |  | 23.4175 |  | 18.487 |  | 11.7544 |  | 5.1493
02/17 24:00:00 | 24.2921 | 26.1246 | 25.7286 | 25.0929 | 24.8988 | 25.2885 | 21.7915 | 22.2173 | 18.3867 | 20.3995 | 19.8929 | 19.1067 | 17.9805 | 17.0935 | [14 empty] | 6.2528 |  | 26.2538 |  |  |  | 1.6724 |  | 10.9302 |  | 7.8372 |  | 4.0533 |  | 0.7869
02/18 01:00:00 | 24.1247 | 25.8478 | 25.5245 | 24.739 | 24.469 | 24.9112 | 21.6759 | 21.133 | 17.7759 | 19.5117 | 19.0291 | 18.3039 | 17.2405 | 17.5938 | [14 empty] | 5.9962 |  | 12.5254 |  |  |  | 0.03314 |  | 3.6783 |  | 2.0601 |  | 0.50421 |  | 0.12483
02/18 02:00:00 | 23.9164 | 25.5632 | 25.3188 | 24.4082 | 24.0707 | 24.5672 | 21.5878 | 20.9126 | 17.293 | 19.0861 | 18.8914 | 18.2331 | 17.1721 | 18.6783 | [14 empty] | 5.4223 |  | 4.9922 |  |  |  | 1.9189 |  | 0.1663 |  | 0.04542 |  | 0.19815 |  | 2.2686
02/18 03:00:00 | 23.6882 | 25.2646 | 25.1027 | 24.0704 | 23.7256 | 24.2838 | 21.5088 | 16.526 | 16.7448 | 18.331 | 18.0449 | 17.4443 | 16.434 | 18.7311 | [14 empty] | 4.7498 |  | 4.8628 |  |  |  | 3.9457 |  | 0.16007 |  | 0.47085 |  | 1.656 |  | 5.277
02/18 04:00:00 | 23.4802 | 25.022 | 24.8862 | 23.8056 | 23.3923 | 24.0239 | 21.458 | 19.4734 | 16.1555 | 17.5574 | 17.2237 | 16.6664 | 15.6823 | 19.2037 | [14 empty] | 4.0892 |  | 0.072703 |  |  |  | 9.2916 |  | 2.7106 |  | 3.9208 |  | 6.4379 |  | 12.4004
02/18 05:00:00 | 23.2859 | 24.78 | 24.6449 | 23.534 | 23.1037 | 23.7396 | 21.3977 | 14.871 | 15.5137 | 16.7053 | 16.2609 | 15.7594 | 14.8189 | 19.5441 | [14 empty] | 3.5653 |  | 21.8382 |  |  |  | 16.2441 |  | 8.0588 |  | 10.7793 |  | 14.324 |  | 22.3277
02/18 06:00:00 | 23.0622 | 24.5423 | 24.4162 | 23.2721 | 22.8424 | 23.4657 | 21.3994 | 14.5754 | 12.7843 | 13.1643 | 13.6859 | 13.4504 | 12.5952 | 19.4303 | [14 empty] | 2.7648 |  | 23.5707 |  |  |  | 44.169 |  | 39.2628 |  | 32.9979 |  | 35.7592 |  | 46.7195
02/18 07:00:00 | 22.9476 | 24.3874 | 24.2732 | 23.1113 | 22.6827 | 23.2991 | 21.4201 | 14.3322 | 12.6572 | 13.1595 | 13.6236 | 13.3464 | 12.5463 | 19.0237 | [14 empty] | 2.333 |  | 22.0108 |  |  |  | 40.5325 |  | 34.3889 |  | 29.1614 |  | 32.2321 |  | 41.9571
02/18 08:00:00 | 22.8201 | 24.2703 | 24.1624 | 22.9876 | 22.5566 | 23.1725 | 21.481 | 13.2801 | 14.3127 | 15.239 | 14.5299 | 14.0433 | 13.212 | 17.5499 | [14 empty] | 1.7931 |  | 18.2318 |  |  |  | 10.4795 |  | 5.3403 |  | 9.1205 |  | 12.2965 |  | 18.8175
02/18 09:00:00 | 22.6838 | 24.1123 | 24.0255 | 22.8165 | 22.3792 | 22.9974 | 22.2065 | 15.5238 | 17.6091 | 15.0461 | 14.9653 | 16.8018 | 13.7464 | 30.2407 | [14 empty] | 0.22779 |  | 216.5888 |  |  |  | 159.5579 |  | 230.8761 |  | 233.3397 |  | 180.6057 |  | 272.0645
02/18 10:00:00 | 22.5737 | 23.9425 | 23.8881 | 22.6548 | 22.2001 | 22.8383 | 23.0237 | 14.8589 | 14.8854 | 14.949 | 13.2209 | 12.5485 | 11.6279 | 3.6664 | [14 empty] | 0.2025 |  | 125.2714 |  |  |  | 125.8655 |  | 127.2979 |  | 91.2882 |  | 78.8915 |  | 63.3849
02/18 11:00:00 | 22.5672 | 23.951 | 23.9408 | 22.6406 | 22.1966 | 22.8621 | 23.4383 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0416 | [14 empty] | 0.75872 |  | 9.2514 |  |  |  | 9.2514 |  | 9.2514 |  | 9.2514 |  | 9.2514 |  | 9.2514
02/18 12:00:00 | 22.2837 | 23.8658 | 23.7975 | 22.4892 | 22.1702 | 22.8716 | 23.7487 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9006 | [14 empty] | 2.1461 |  | 8.4133 |  |  |  | 8.4133 |  | 8.4133 |  | 8.4133 |  | 8.4133 |  | 8.4133
02/18 13:00:00 | 22.0915 | 23.7849 | 23.7005 | 22.402 | 22.1534 | 22.8999 | 24.0342 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8233 | [14 empty] | 3.774 |  | 7.9711 |  |  |  | 7.9711 |  | 7.9711 |  | 7.9711 |  | 7.9711 |  | 7.9711
02/18 14:00:00 | 22.1318 | 23.8402 | 23.7762 | 22.4732 | 22.2476 | 23.0314 | 24.3255 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8328 | [14 empty] | 4.8122 |  | 8.025 |  |  |  | 8.025 |  | 8.025 |  | 8.025 |  | 8.025 |  | 8.025
02/18 15:00:00 | 22.2586 | 23.9751 | 23.9208 | 22.6114 | 22.4004 | 23.2211 | 24.6299 | 0 | 0 | 0 | 0 | 0 | 0 | 2.796 | [14 empty] | 5.6229 |  | 7.8174 |  |  |  | 7.8174 |  | 7.8174 |  | 7.8174 |  | 7.8174 |  | 7.8174
02/18 16:00:00 | 22.4487 | 24.186 | 24.1222 | 22.8065 | 22.6063 | 23.472 | 24.9236 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8664 | [14 empty] | 6.1251 |  | 8.2165 |  |  |  | 8.2165 |  | 8.2165 |  | 8.2165 |  | 8.2165 |  | 8.2165
02/18 17:00:00 | 22.6541 | 24.425 | 24.3724 | 23.0517 | 22.8647 | 23.7376 | 25.0456 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7835 | [14 empty] | 5.7192 |  | 7.7478 |  |  |  | 7.7478 |  | 7.7478 |  | 7.7478 |  | 7.7478 |  | 7.7478
02/18 18:00:00 | 22.8333 | 24.6188 | 24.5651 | 23.2443 | 23.0679 | 23.9504 | 24.9939 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8372 | [14 empty] | 4.6682 |  | 8.0497 |  |  |  | 8.0497 |  | 8.0497 |  | 8.0497 |  | 8.0497 |  | 8.0497
02/18 19:00:00 | 23.0145 | 24.8192 | 24.7292 | 23.4137 | 23.2477 | 24.1525 | 24.5804 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9427 | [14 empty] | 2.452 |  | 8.6597 |  |  |  | 8.6597 |  | 8.6597 |  | 8.6597 |  | 8.6597 |  | 8.6597
02/18 20:00:00 | 23.0222 | 24.8574 | 24.7141 | 23.4034 | 23.2447 | 24.1371 | 24.1727 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9338 | [14 empty] | 1.3235 |  | 8.607 |  |  |  | 8.607 |  | 8.607 |  | 8.607 |  | 8.607 |  | 8.607
02/18 21:00:00 | 22.8865 | 24.698 | 24.5449 | 23.233 | 23.074 | 23.9355 | 23.8669 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9493 | [14 empty] | 0.96117 |  | 8.6983 |  |  |  | 8.6983 |  | 8.6983 |  | 8.6983 |  | 8.6983 |  | 8.6983
02/18 22:00:00 | 22.7085 | 24.5055 | 24.3809 | 23.0679 | 22.8708 | 23.7194 | 23.5655 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8888 | [14 empty] | 0.7345 |  | 8.345 |  |  |  | 8.345 |  | 8.345 |  | 8.345 |  | 8.345 |  | 8.345
02/18 23:00:00 | 22.5522 | 24.3255 | 24.2146 | 22.9005 | 22.691 | 23.53 | 23.2458 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9547 | [14 empty] | 0.48118 |  | 8.7302 |  |  |  | 8.7302 |  | 8.7302 |  | 8.7302 |  | 8.7302 |  | 8.7302
02/18 24:00:00 | 22.3959 | 24.1452 | 24.0323 | 22.7166 | 22.5108 | 23.3408 | 22.9804 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9365 | [14 empty] | 0.34164 |  | 8.6233 |  |  |  | 8.6233 |  | 8.6233 |  | 8.6233 |  | 8.6233 |  | 8.6233
02/19 01:00:00 | 22.2228 | 23.9446 | 23.832 | 22.5142 | 22.3118 | 23.1326 | 22.6622 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8627 | [14 empty] | 0.19302 |  | 8.1951 |  |  |  | 8.1951 |  | 8.1951 |  | 8.1951 |  | 8.1951 |  | 8.1951
02/19 02:00:00 | 22.0154 | 23.7102 | 23.5984 | 22.2771 | 22.0752 | 22.887 | 22.4366 | 0 | 0 | 0 | 0 | 0 | 0 | 13.5207 | [14 empty] | 0.17739 |  | 182.8083 |  |  |  | 182.8083 |  | 182.8083 |  | 182.8083 |  | 182.8083 |  | 182.8083
02/19 03:00:00 | 21.7929 | 23.4585 | 23.3513 | 22.0246 | 21.8209 | 22.6243 | 22.3533 | 0 | 0 | 0 | 0 | 0 | 0 | 11.4876 | [14 empty] | 0.31401 |  | 131.965 |  |  |  | 131.965 |  | 131.965 |  | 131.965 |  | 131.965 |  | 131.965
02/19 04:00:00 | 21.6223 | 23.2071 | 23.1113 | 21.7787 | 21.572 | 22.3687 | 22.2698 | 0 | 0 | 0 | 0 | 0 | 0 | 11.4289 | [14 empty] | 0.41936 |  | 130.6206 |  |  |  | 130.6206 |  | 130.6206 |  | 130.6206 |  | 130.6206 |  | 130.6206
02/19 05:00:00 | 21.4975 | 22.9608 | 22.9305 | 21.5932 | 21.385 | 22.1249 | 22.1774 | 18.3667 | 19.9271 | 18.5281 | 19.1578 | 20.1517 | 18.03 | 12.8587 | [14 empty] | 0.46224 |  | 30.3387 |  |  |  | 49.9628 |  | 32.1422 |  | 39.6792 |  | 53.1882 |  | 26.7432
02/19 06:00:00 | 21.5499 | 22.9122 | 22.979 | 21.6032 | 21.3804 | 22.0566 | 22.0821 | 11.7141 | 10.3604 | 10.6198 | 10.9721 | 12.5268 | 10.1283 | 13.6386 | [14 empty] | 0.28318 |  | 3.7041 |  |  |  | 10.747 |  | 9.1136 |  | 7.1107 |  | 1.2363 |  | 12.3228
02/19 07:00:00 | 21.5363 | 22.8833 | 22.9605 | 21.5502 | 21.3233 | 21.9977 | 22.0158 | 11.5338 | 9.8119 | 10.393 | 10.678 | 12.7158 | 9.7999 | 12.9743 | [14 empty] | 0.22991 |  | 2.075 |  |  |  | 10.0003 |  | 6.6631 |  | 5.273 |  | 0.066801 |  | 10.0765
02/19 08:00:00 | 21.4922 | 22.8356 | 22.9095 | 21.4862 | 21.2641 | 21.9275 | 21.9901 | 11.25 | 9.561 | 10.2024 | 10.4388 | 13.0003 | 9.5937 | 14.1196 | [14 empty] | 0.24794 |  | 8.2348 |  |  |  | 20.7811 |  | 15.3446 |  | 13.5482 |  | 1.2529 |  | 20.484
02/19 09:00:00 | 21.4376 | 22.767 | 22.8475 | 21.4107 | 21.1997 | 21.8437 | 22.1211 | 13.3577 | 12.5897 | 12.6694 | 12.6966 | 17.5214 | 11.6089 | 20.2163 | [14 empty] | 0.46705 |  | 47.0406 |  |  |  | 58.1662 |  | 56.9562 |  | 56.5472 |  | 7.2629 |  | 74.0889
02/19 10:00:00 | 21.3748 | 22.7084 | 22.7775 | 21.328 | 21.1637 | 21.7536 | 22.4332 | 24.0503 | 11.8321 | 11.8734 | 38.411 | 48.3636 | 10.7961 | 12.9317 | [14 empty] | 1.1201 |  | 123.6242 |  |  |  | 1.2092 |  | 1.1199 |  | 649.1968 |  | 1255.4178 |  | 4.5607
02/19 11:00:00 | 21.4303 | 22.6607 | 22.7273 | 21.5081 | 21.4858 | 21.6932 | 22.8361 | 45.6676 | 12.0913 | 12.2801 | 54.0199 | 55.0738 | 40.4191 | 4.203 | [14 empty] | 1.9764 |  | 1719.3134 |  |  |  | 62.2255 |  | 65.24 |  | 2481.7191 |  | 2587.8417 |  | 1311.6077
02/19 12:00:00 | 22.0001 | 22.6472 | 22.7248 | 22.6477 | 23.1093 | 21.8784 | 23.2989 | 0 | 0 | 0 | 0 | 0 | 0 | 2.967 | [14 empty] | 1.6871 |  | 8.8029 |  |  |  | 8.8029 |  | 8.8029 |  | 8.8029 |  | 8.8029 |  | 8.8029
02/19 13:00:00 | 21.9299 | 22.5544 | 22.6026 | 23.2122 | 23.86 | 22.1373 | 23.7125 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4577 | [14 empty] | 3.1777 |  | 2.1249 |  |  |  | 2.1249 |  | 2.1249 |  | 2.1249 |  | 2.1249 |  | 2.1249
02/19 14:00:00 | 21.7543 | 22.5908 | 22.624 | 23.2071 | 23.5719 | 22.3233 | 24.0909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 5.4595 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/19 15:00:00 | 21.8041 | 22.7758 | 22.8149 | 23.3006 | 23.5637 | 22.5677 | 24.4617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 7.0627 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/19 16:00:00 | 21.9351 | 22.9872 | 23.0303 | 23.4692 | 23.6693 | 22.7995 | 24.8192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 8.3181 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/19 17:00:00 | 22.0929 | 23.1908 | 23.2315 | 23.6493 | 23.8164 | 23.0243 | 25.0503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 8.7462 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/19 18:00:00 | 22.3169 | 23.4067 | 23.4803 | 23.8802 | 24.0332 | 23.2838 | 25.0759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 7.6123 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/19 19:00:00 | 22.5857 | 23.7559 | 23.7928 | 24.139 | 24.2692 | 23.6408 | 24.7031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.4834 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/19 20:00:00 | 22.6598 | 23.9239 | 23.8778 | 24.1795 | 24.2824 | 23.7914 | 24.2734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.6038 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/19 21:00:00 | 22.5679 | 23.8171 | 23.7654 | 24.0501 | 24.1017 | 23.6824 | 23.8881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.743 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/19 22:00:00 | 22.3926 | 23.6426 | 23.575 | 23.8393 | 23.8253 | 23.4949 | 23.5497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.339 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/19 23:00:00 | 22.2199 | 23.4284 | 23.3887 | 23.5907 | 23.5626 | 23.3133 | 23.2314 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6249 | [14 empty] | 1.0231 |  | 13.14 |  |  |  | 13.14 |  | 13.14 |  | 13.14 |  | 13.14 |  | 13.14
02/19 24:00:00 | 22.0441 | 23.2312 | 23.1982 | 23.3271 | 23.2893 | 23.1259 | 22.908 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9634 | [14 empty] | 0.74634 |  | 8.7815 |  |  |  | 8.7815 |  | 8.7815 |  | 8.7815 |  | 8.7815 |  | 8.7815
02/20 01:00:00 | 21.8382 | 22.9851 | 22.977 | 23.0345 | 22.982 | 22.9041 | 22.593 | 0 | 0 | 0 | 0 | 0 | 0 | 12.4833 | [14 empty] | 0.56963 |  | 155.8317 |  |  |  | 155.8317 |  | 155.8317 |  | 155.8317 |  | 155.8317 |  | 155.8317
02/20 02:00:00 | 21.6524 | 22.7638 | 22.7758 | 22.8199 | 22.7525 | 22.6995 | 22.4468 | 39.4843 | 14.8254 | 13.7861 | 43.8333 | 47.1454 | 33.7731 | 11.0084 | [14 empty] | 0.63113 |  | 810.877 |  |  |  | 14.5694 |  | 7.7155 |  | 1077.4718 |  | 1305.883 |  | 518.2318
02/20 03:00:00 | 22.4547 | 22.6965 | 22.7159 | 23.5398 | 23.4442 | 23.0914 | 22.4062 | 29.5643 | 8.8247 | 9.6268 | 28.0359 | 28.4482 | 19.6655 | 10.5884 | [14 empty] | 0.0023576 |  | 360.0833 |  |  |  | 3.1108 |  | 0.92471 |  | 304.415 |  | 318.9723 |  | 82.3942
02/20 04:00:00 | 23.1289 | 22.6283 | 22.6557 | 24.0571 | 23.9528 | 23.317 | 22.2367 | 28.0237 | 8.189 | 9.1955 | 26.6636 | 26.9413 | 19.2154 | 12.7075 | [14 empty] | 0.79594 |  | 234.5842 |  |  |  | 20.4173 |  | 12.3346 |  | 194.7728 |  | 202.6003 |  | 42.3519
02/20 05:00:00 | 23.3656 | 22.5287 | 22.5589 | 24.1898 | 24.0829 | 23.3453 | 22.139 | 26.7016 | 7.9747 | 8.9555 | 25.5079 | 25.7857 | 18.5819 | 13.0743 | [14 empty] | 1.5044 |  | 185.7027 |  |  |  | 26.0058 |  | 16.9647 |  | 154.5939 |  | 161.579 |  | 30.3338
02/20 06:00:00 | 23.4217 | 22.3888 | 22.4213 | 24.199 | 24.0845 | 23.2933 | 22.0356 | 25.2908 | 7.8463 | 8.744 | 24.1981 | 24.4776 | 17.7436 | 13.0493 | [14 empty] | 1.9212 |  | 149.8533 |  |  |  | 27.0717 |  | 18.5358 |  | 124.2966 |  | 130.6066 |  | 22.0361
02/20 07:00:00 | 23.3889 | 22.2115 | 22.2409 | 24.1177 | 23.9935 | 23.1735 | 21.9298 | 23.8086 | 7.6148 | 8.4621 | 22.8098 | 23.0768 | 16.7946 | 15.2604 | [14 empty] | 2.1289 |  | 73.0719 |  |  |  | 58.4556 |  | 46.2171 |  | 56.9922 |  | 61.0958 |  | 2.3537
02/20 08:00:00 | 23.3017 | 22.0118 | 22.0369 | 23.9819 | 23.8466 | 23.0119 | 21.9625 | 23.2998 | 9.928 | 9.0267 | 28.681 | 30.0211 | 19.2236 | 22.7963 | [14 empty] | 1.7936 |  | 0.25357 |  |  |  | 165.5926 |  | 189.6022 |  | 34.6298 |  | 52.1987 |  | 12.7642
02/20 09:00:00 | 23.1885 | 21.8335 | 21.8919 | 23.8848 | 23.7603 | 22.893 | 22.1981 | 26.0168 | 17.0925 | 13.0291 | 25.788 | 26.3203 | 19.4525 | 15.0956 | [14 empty] | 0.98098 |  | 119.2723 |  |  |  | 3.9879 |  | 4.2702 |  | 114.3282 |  | 125.9954 |  | 18.9826
02/20 10:00:00 | 23.2524 | 21.8479 | 21.9314 | 23.9305 | 23.8354 | 22.9406 | 22.4919 | 23.3078 | 29.8437 | 24.881 | 23.1207 | 23.4375 | 17.0286 | 14.1041 | [14 empty] | 0.57838 |  | 84.7079 |  |  |  | 247.7337 |  | 116.1412 |  | 81.2991 |  | 87.1129 |  | 8.5525
02/20 11:00:00 | 23.4739 | 22.3834 | 22.3976 | 24.1662 | 24.1123 | 23.1634 | 22.9114 | 21.3347 | 31.2769 | 29.7701 | 21.0427 | 21.2933 | 15.421 | 4.5252 | [14 empty] | 0.31639 |  | 282.5611 |  |  |  | 715.6551 |  | 637.307 |  | 272.8283 |  | 281.1698 |  | 118.7206
02/20 12:00:00 | 23.756 | 23.6518 | 23.2289 | 24.4547 | 24.4327 | 23.4572 | 23.5462 | 17.6376 | 21.3946 | 21.5506 | 17.2548 | 17.3408 | 11.8348 | 3.1361 | [14 empty] | 0.044039 |  | 210.2935 |  |  |  | 333.373 |  | 339.0919 |  | 199.3375 |  | 201.7726 |  | 75.667
02/20 13:00:00 | 24.5674 | 25.8199 | 24.909 | 25.3061 | 25.3249 | 24.4117 | 23.9661 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8255 | [14 empty] | 0.36161 |  | 7.9835 |  |  |  | 7.9835 |  | 7.9835 |  | 7.9835 |  | 7.9835 |  | 7.9835
02/20 14:00:00 | 24.5068 | 26.3345 | 25.0774 | 25.3981 | 25.4532 | 24.652 | 24.3216 | 0 | 0 | 0 | 0 | 0 | 0 | 2.766 | [14 empty] | 0.034294 |  | 7.6508 |  |  |  | 7.6508 |  | 7.6508 |  | 7.6508 |  | 7.6508 |  | 7.6508
02/20 15:00:00 | 24.3414 | 26.2446 | 24.9087 | 25.3482 | 25.4286 | 24.7543 | 24.6984 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8107 | [14 empty] | 0.12747 |  | 7.9002 |  |  |  | 7.9002 |  | 7.9002 |  | 7.9002 |  | 7.9002 |  | 7.9002
02/20 16:00:00 | 24.7049 | 26.6478 | 25.3011 | 25.6895 | 25.8238 | 25.2539 | 24.9368 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7544 | [14 empty] | 0.053783 |  | 7.5869 |  |  |  | 7.5869 |  | 7.5869 |  | 7.5869 |  | 7.5869 |  | 7.5869
02/20 17:00:00 | 25.0199 | 27.028 | 25.6288 | 25.9815 | 26.136 | 25.634 | 25.0899 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7635 | [14 empty] | 0.0048925 |  | 7.637 |  |  |  | 7.637 |  | 7.637 |  | 7.637 |  | 7.637 |  | 7.637
02/20 18:00:00 | 25.1412 | 27.1844 | 25.7494 | 26.1274 | 26.2661 | 25.797 | 24.8982 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8032 | [14 empty] | 0.059053 |  | 7.858 |  |  |  | 7.858 |  | 7.858 |  | 7.858 |  | 7.858 |  | 7.858
02/20 19:00:00 | 25.125 | 27.202 | 25.7181 | 26.1338 | 26.2493 | 25.8164 | 24.4733 | 0 | 0 | 0 | 0 | 0 | 0 | 2.851 | [14 empty] | 0.42478 |  | 8.1281 |  |  |  | 8.1281 |  | 8.1281 |  | 8.1281 |  | 8.1281 |  | 8.1281
02/20 20:00:00 | 24.7027 | 26.8278 | 25.2569 | 25.7354 | 25.7795 | 25.3553 | 24.0257 | 0 | 0 | 0 | 0 | 0 | 0 | 2.878 | [14 empty] | 0.45838 |  | 8.2826 |  |  |  | 8.2826 |  | 8.2826 |  | 8.2826 |  | 8.2826 |  | 8.2826
02/20 21:00:00 | 24.1213 | 26.3116 | 24.7485 | 25.1675 | 25.2159 | 24.841 | 23.6583 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8979 | [14 empty] | 0.21434 |  | 8.3979 |  |  |  | 8.3979 |  | 8.3979 |  | 8.3979 |  | 8.3979 |  | 8.3979
02/20 22:00:00 | 23.6757 | 25.8832 | 24.3169 | 24.7231 | 24.7706 | 24.4253 | 23.3329 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8227 | [14 empty] | 0.1175 |  | 7.9679 |  |  |  | 7.9679 |  | 7.9679 |  | 7.9679 |  | 7.9679 |  | 7.9679
02/20 23:00:00 | 23.3606 | 25.4982 | 23.9989 | 24.333 | 24.3752 | 24.0377 | 23.0395 | 0 | 0 | 0 | 0 | 0 | 0 | 2.91 | [14 empty] | 0.10315 |  | 8.4682 |  |  |  | 8.4682 |  | 8.4682 |  | 8.4682 |  | 8.4682 |  | 8.4682
02/20 24:00:00 | 23.0962 | 25.2069 | 23.7292 | 24.0528 | 24.0197 | 23.7551 | 22.7403 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9348 | [14 empty] | 0.12665 |  | 8.613 |  |  |  | 8.613 |  | 8.613 |  | 8.613 |  | 8.613 |  | 8.613
02/21 01:00:00 | 22.8527 | 24.9585 | 23.4822 | 23.8155 | 23.7609 | 23.5154 | 22.5026 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2992 | [14 empty] | 0.12257 |  | 106.0733 |  |  |  | 106.0733 |  | 106.0733 |  | 106.0733 |  | 106.0733 |  | 106.0733
02/21 02:00:00 | 22.6513 | 24.7435 | 23.2794 | 23.6171 | 23.559 | 23.3151 | 22.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3026 | [14 empty] | 0.055939 |  | 106.1434 |  |  |  | 106.1434 |  | 106.1434 |  | 106.1434 |  | 106.1434 |  | 106.1434
02/21 03:00:00 | 22.4522 | 24.5261 | 23.0788 | 23.4147 | 23.3509 | 23.111 | 22.4195 | 21.2908 | 26.3637 | 24.6477 | 23.1592 | 24.8768 | 17.8651 | 10.9399 | [14 empty] | 0.0010697 |  | 107.143 |  |  |  | 237.8936 |  | 187.9047 |  | 149.3114 |  | 194.2394 |  | 47.9597
02/21 04:00:00 | 22.537 | 24.5914 | 23.2225 | 23.4623 | 23.3885 | 23.0757 | 22.4092 | 14.2091 | 16.1732 | 17.4227 | 15.7161 | 15.8456 | 11.6507 | 9.8141 | [14 empty] | 0.016334 |  | 19.3163 |  |  |  | 40.4381 |  | 57.8915 |  | 34.8343 |  | 36.3793 |  | 3.3732
02/21 05:00:00 | 22.5948 | 24.6785 | 23.3771 | 23.5124 | 23.4273 | 23.0309 | 22.3184 | 13.7988 | 14.8949 | 13.6863 | 14.7309 | 14.7611 | 10.99 | 11.8059 | [14 empty] | 0.076357 |  | 3.9715 |  |  |  | 9.5418 |  | 3.5359 |  | 8.5554 |  | 8.7333 |  | 0.66576
02/21 06:00:00 | 22.59 | 24.7133 | 23.4203 | 23.4981 | 23.4006 | 22.9457 | 22.2553 | 13.4448 | 12.3234 | 13.4791 | 12.7606 | 14.2259 | 9.7373 | 11.0166 | [14 empty] | 0.11201 |  | 5.8959 |  |  |  | 1.7076 |  | 6.0639 |  | 3.0414 |  | 10.2994 |  | 1.6366
02/21 07:00:00 | 22.5704 | 24.6994 | 23.4152 | 23.4487 | 23.3336 | 22.8586 | 22.2071 | 12.4193 | 14.1382 | 12.7893 | 11.9192 | 13.1111 | 9.0728 | 13.0102 | [14 empty] | 0.13202 |  | 0.34917 |  |  |  | 1.2724 |  | 0.04879 |  | 1.1902 |  | 0.010192 |  | 15.5034
02/21 08:00:00 | 22.5342 | 24.6719 | 23.3907 | 23.3898 | 23.2186 | 22.7802 | 22.2503 | 14.8911 | 15.5305 | 15.9334 | 14.8582 | 15.0675 | 11.1575 | 18.8072 | [14 empty] | 0.080609 |  | 15.3352 |  |  |  | 10.7362 |  | 8.2585 |  | 15.5943 |  | 13.9847 |  | 58.5171
02/21 09:00:00 | 22.5017 | 24.6317 | 23.3722 | 23.3354 | 23.1323 | 22.7125 | 22.5394 | 15.2601 | 16.3505 | 16.8664 | 14.219 | 14.3128 | 10.2829 | 11.7731 | [14 empty] | 0.001418 |  | 12.1586 |  |  |  | 20.9524 |  | 25.9409 |  | 5.9824 |  | 6.4498 |  | 2.2209
02/21 10:00:00 | 22.6689 | 24.7559 | 23.5754 | 23.4504 | 23.2512 | 22.819 | 22.8025 | 13.4762 | 14.5089 | 14.8988 | 12.4391 | 12.5286 | 8.7984 | 3.336 | [14 empty] | 0.017839 |  | 102.823 |  |  |  | 124.8329 |  | 133.697 |  | 82.8655 |  | 84.5028 |  | 29.8376
02/21 11:00:00 | 23.0843 | 25.116 | 24.0438 | 23.7992 | 23.6065 | 23.1691 | 23.0644 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0809 | [14 empty] | 0.00039572 |  | 9.4918 |  |  |  | 9.4918 |  | 9.4918 |  | 9.4918 |  | 9.4918 |  | 9.4918
02/21 12:00:00 | 23.4308 | 25.5081 | 24.4139 | 24.1375 | 23.9655 | 23.5908 | 23.4559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.00062931 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/21 13:00:00 | 23.6724 | 25.7963 | 24.6596 | 24.386 | 24.2309 | 23.933 | 23.8054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.017691 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/21 14:00:00 | 23.6897 | 25.8622 | 24.6605 | 24.4184 | 24.2745 | 24.0764 | 24.0565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.1345 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/21 15:00:00 | 23.7775 | 25.9929 | 24.767 | 24.5399 | 24.4038 | 24.2777 | 24.2662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.23877 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/21 16:00:00 | 24.1435 | 26.3615 | 25.2173 | 24.9268 | 24.7952 | 24.7571 | 24.477 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.11122 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/21 17:00:00 | 24.4442 | 26.6517 | 25.5446 | 25.2126 | 25.0842 | 25.1044 | 24.6443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.040063 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/21 18:00:00 | 24.5232 | 26.7364 | 25.5961 | 25.2832 | 25.1554 | 25.1751 | 24.6334 | 0 | 0 | 0 | 0 | 0 | 0 | 18.8968 | [14 empty] | 0.012141 |  | 357.0884 |  |  |  | 357.0884 |  | 357.0884 |  | 357.0884 |  | 357.0884 |  | 357.0884
02/21 19:00:00 | 24.4979 | 26.7143 | 25.5473 | 25.2512 | 25.1143 | 25.1354 | 24.5898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.0084392 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/21 20:00:00 | 24.2845 | 26.4554 | 25.3079 | 25.0321 | 24.8735 | 24.8962 | 24.3945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.012098 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/21 21:00:00 | 23.9767 | 26.064 | 24.9186 | 24.7165 | 24.5038 | 24.5278 | 24.1556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.031991 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/21 22:00:00 | 23.7022 | 25.7675 | 24.5825 | 24.4351 | 24.1838 | 24.2079 | 23.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.07662 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/21 23:00:00 | 23.5209 | 25.5845 | 24.3869 | 24.2477 | 23.996 | 24.0199 | 23.8038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.080052 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/21 24:00:00 | 23.3413 | 25.4018 | 24.2023 | 24.0589 | 23.8136 | 23.8386 | 23.6334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.085331 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 01:00:00 | 23.1571 | 25.1561 | 24.0113 | 23.8104 | 23.5702 | 23.5972 | 23.4916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.11189 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 02:00:00 | 23.0559 | 24.9965 | 23.9055 | 23.6554 | 23.4168 | 23.4459 | 23.3618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.093585 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 03:00:00 | 22.9348 | 24.8298 | 23.7779 | 23.5332 | 23.2545 | 23.2865 | 23.2831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.12126 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 04:00:00 | 22.8122 | 24.659 | 23.648 | 23.3647 | 23.0868 | 23.1218 | 23.1372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.10559 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 05:00:00 | 22.6919 | 24.5403 | 23.5201 | 23.1976 | 22.9693 | 23.0069 | 23.0036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.097181 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 06:00:00 | 22.5687 | 24.4178 | 23.3892 | 23.0779 | 22.8474 | 22.8878 | 22.8715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.091719 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 07:00:00 | 22.4443 | 24.2917 | 23.2572 | 22.9571 | 22.7215 | 22.7649 | 22.7432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.089311 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 08:00:00 | 22.3263 | 24.1688 | 23.1319 | 22.8403 | 22.6004 | 22.647 | 22.6332 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5799 | [14 empty] | 0.094185 |  | 2.4962 |  |  |  | 2.4962 |  | 2.4962 |  | 2.4962 |  | 2.4962 |  | 2.4962
02/22 09:00:00 | 22.2318 | 24.0651 | 23.0317 | 22.7458 | 22.5019 | 22.5521 | 22.5865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.12577 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 10:00:00 | 22.2318 | 24.0401 | 23.03 | 22.7418 | 22.4922 | 22.5495 | 22.6594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.18282 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 11:00:00 | 22.4045 | 24.1573 | 23.209 | 22.908 | 22.6549 | 22.7221 | 22.9537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.30159 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 12:00:00 | 22.6793 | 24.4287 | 23.5391 | 23.2177 | 22.9659 | 23.0486 | 23.4025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.52292 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 13:00:00 | 23.0707 | 24.9058 | 24.0135 | 23.627 | 23.4224 | 23.5769 | 23.737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.44396 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 14:00:00 | 23.195 | 25.0844 | 24.1434 | 23.7324 | 23.5556 | 23.7577 | 24.1548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.92121 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 15:00:00 | 23.3684 | 25.257 | 24.3167 | 23.9213 | 23.7311 | 23.961 | 24.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.6993 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 16:00:00 | 23.8947 | 25.7787 | 24.8561 | 24.4505 | 24.2572 | 24.51 | 25.149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.5733 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 17:00:00 | 24.517 | 26.5246 | 25.5052 | 25.0914 | 24.9107 | 25.2221 | 25.5551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.0777 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 18:00:00 | 24.825 | 26.9567 | 25.8387 | 25.4285 | 25.2585 | 25.6054 | 25.6181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.62905 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 19:00:00 | 24.8452 | 27.006 | 25.8638 | 25.4646 | 25.2786 | 25.632 | 25.3778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.28373 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 20:00:00 | 24.5501 | 26.6628 | 25.5391 | 25.1556 | 24.9179 | 25.2724 | 25.1699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.38421 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 21:00:00 | 24.1343 | 26.2269 | 25.0967 | 24.6949 | 24.4042 | 24.7506 | 24.9303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.63355 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 22:00:00 | 23.8236 | 25.9262 | 24.7666 | 24.3316 | 24.0648 | 24.4036 | 24.7318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.82484 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 23:00:00 | 23.5625 | 25.6168 | 24.4865 | 24.0721 | 23.8127 | 24.1467 | 24.5949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.0659 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/22 24:00:00 | 23.3151 | 25.3216 | 24.2203 | 23.8225 | 23.566 | 23.8965 | 24.3582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.0881 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 01:00:00 | 23.0796 | 25.0709 | 23.9672 | 23.5812 | 23.3248 | 23.6528 | 24.1295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.1022 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 02:00:00 | 22.8853 | 24.8543 | 23.7577 | 23.3782 | 23.12 | 23.4457 | 23.9685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.1733 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 03:00:00 | 22.699 | 24.6417 | 23.5575 | 23.1817 | 22.92 | 23.2441 | 23.8682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.3669 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 04:00:00 | 22.5146 | 24.4299 | 23.3607 | 22.9853 | 22.7196 | 23.0429 | 23.7187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.4498 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 05:00:00 | 22.335 | 24.2217 | 23.1696 | 22.7937 | 22.5234 | 22.8466 | 23.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.4115 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 06:00:00 | 22.1492 | 24.0083 | 22.9734 | 22.5951 | 22.32 | 22.6442 | 23.3945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.5509 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 07:00:00 | 21.9604 | 23.7924 | 22.7748 | 22.393 | 22.1145 | 22.4407 | 23.3047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.807 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 08:00:00 | 21.8199 | 23.6313 | 22.6282 | 22.2432 | 21.9622 | 22.2908 | 23.1886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.8733 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 09:00:00 | 21.7409 | 23.5363 | 22.5461 | 22.1568 | 21.8738 | 22.2047 | 23.1316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.9341 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 10:00:00 | 21.7733 | 23.5274 | 22.581 | 22.1758 | 21.8863 | 22.224 | 23.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.2489 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 11:00:00 | 21.9808 | 23.6701 | 22.8521 | 22.368 | 22.0789 | 22.422 | 23.7262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.0464 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 12:00:00 | 22.4221 | 24.108 | 23.3834 | 22.8484 | 22.568 | 22.9255 | 24.1904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.1269 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 13:00:00 | 23.0611 | 24.8962 | 24.0576 | 23.4845 | 23.2583 | 23.7156 | 24.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.3344 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 14:00:00 | 23.2676 | 25.183 | 24.2319 | 23.658 | 23.4531 | 23.9567 | 24.7704 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1647 | [14 empty] | 2.2583 |  | 1.3565 |  |  |  | 1.3565 |  | 1.3565 |  | 1.3565 |  | 1.3565 |  | 1.3565
02/23 15:00:00 | 23.3693 | 25.2966 | 24.3125 | 23.7548 | 23.543 | 24.0627 | 24.8565 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4374 | [14 empty] | 2.2116 |  | 29.565 |  |  |  | 29.565 |  | 29.565 |  | 29.565 |  | 29.565 |  | 29.565
02/23 16:00:00 | 23.7138 | 25.6945 | 24.6683 | 24.1082 | 23.8929 | 24.4131 | 24.9953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.6422 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 17:00:00 | 23.9769 | 25.9716 | 24.9374 | 24.3738 | 24.1579 | 24.6695 | 25.2389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.5927 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 18:00:00 | 24.0863 | 26.0656 | 25.0453 | 24.4855 | 24.2684 | 24.7781 | 25.2797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.4244 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 19:00:00 | 24.1148 | 26.0851 | 25.0649 | 24.5141 | 24.2967 | 24.8089 | 25.2038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.1858 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 20:00:00 | 23.9217 | 25.825 | 24.8591 | 24.3212 | 24.0559 | 24.5711 | 24.9444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.0457 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 21:00:00 | 23.6497 | 25.5147 | 24.5737 | 24.0484 | 23.7583 | 24.2689 | 24.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.074 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 22:00:00 | 23.3789 | 25.2619 | 24.2856 | 23.7695 | 23.4846 | 23.9911 | 24.4905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.2356 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 23:00:00 | 23.1818 | 25.0692 | 24.0748 | 23.5643 | 23.2831 | 23.7864 | 24.3583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.3841 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/23 24:00:00 | 23.0149 | 24.891 | 23.8945 | 23.3881 | 23.1081 | 23.6078 | 24.2222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.4576 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 01:00:00 | 22.8566 | 24.7157 | 23.7222 | 23.2197 | 22.94 | 23.4355 | 24.1431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.6552 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 02:00:00 | 22.7762 | 24.6189 | 23.6332 | 23.1315 | 22.8513 | 23.3437 | 24.0685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.67 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 03:00:00 | 22.6832 | 24.4696 | 23.4967 | 22.9956 | 22.7138 | 23.2027 | 23.9713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.6593 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 04:00:00 | 22.5957 | 24.3242 | 23.3657 | 22.8651 | 22.5813 | 23.0664 | 23.8456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.5624 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 05:00:00 | 22.4972 | 24.1771 | 23.2321 | 22.7308 | 22.4442 | 22.9265 | 23.6833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.4068 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 06:00:00 | 22.3848 | 24.0159 | 23.0819 | 22.5794 | 22.2897 | 22.7692 | 23.5036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.2517 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 07:00:00 | 22.2707 | 23.8559 | 22.9706 | 22.4292 | 22.136 | 22.6136 | 23.3271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.116 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 08:00:00 | 22.1651 | 23.6996 | 22.8685 | 22.2857 | 21.9886 | 22.4644 | 23.2336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.1418 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 09:00:00 | 22.0855 | 23.616 | 22.7924 | 22.2136 | 21.9147 | 22.3892 | 23.2858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.4406 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 10:00:00 | 22.1232 | 23.6299 | 22.842 | 22.2634 | 21.9633 | 22.4354 | 23.6262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.259 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 11:00:00 | 22.4094 | 23.815 | 23.1546 | 22.565 | 22.269 | 22.7397 | 24.2678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.4536 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 12:00:00 | 23.2167 | 24.6563 | 24.0074 | 23.3947 | 23.161 | 23.6549 | 24.9542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.0189 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 13:00:00 | 23.9856 | 25.7452 | 24.8496 | 24.1996 | 24.0034 | 24.5745 | 25.5644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.4926 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 14:00:00 | 24.1768 | 26.0168 | 25.0728 | 24.4255 | 24.2231 | 24.831 | 26.0127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.3704 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 15:00:00 | 24.3916 | 26.2907 | 25.3273 | 24.692 | 24.4781 | 25.0953 | 26.534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.59 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 16:00:00 | 24.9421 | 26.8836 | 25.9158 | 25.2714 | 25.0601 | 25.6886 | 27.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.247 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 17:00:00 | 25.4061 | 27.3685 | 26.3875 | 25.7376 | 25.5351 | 26.1795 | 27.1866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.1702 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 18:00:00 | 25.6847 | 27.6259 | 26.6677 | 26.0227 | 25.7751 | 26.4355 | 27.2805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.5467 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 19:00:00 | 25.7883 | 27.7742 | 26.7659 | 26.1328 | 25.8829 | 26.5623 | 27.1415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.8312 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 20:00:00 | 25.5936 | 27.6228 | 26.5562 | 25.9409 | 25.6839 | 26.3592 | 26.8177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.4983 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 21:00:00 | 25.2684 | 27.2367 | 26.1754 | 25.582 | 25.3014 | 25.945 | 26.4387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.3697 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 22:00:00 | 24.9063 | 26.8434 | 25.775 | 25.1261 | 24.9364 | 25.546 | 26.1038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.434 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 23:00:00 | 24.5656 | 26.4779 | 25.4159 | 24.7829 | 24.5928 | 25.207 | 25.835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.6114 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/24 24:00:00 | 24.3554 | 26.2098 | 25.1937 | 24.5771 | 24.3762 | 24.9911 | 25.5944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.535 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/25 01:00:00 | 24.1904 | 26.0266 | 25.0159 | 24.4132 | 24.2016 | 24.8141 | 25.4035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.4717 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/25 02:00:00 | 24.0349 | 25.8458 | 24.8476 | 24.2552 | 24.0342 | 24.6429 | 25.2284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.4243 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/25 03:00:00 | 23.8767 | 25.6584 | 24.676 | 24.0915 | 23.8619 | 24.4663 | 25.0604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.4012 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/25 04:00:00 | 23.7095 | 25.4609 | 24.4952 | 23.9164 | 23.6789 | 24.279 | 24.9405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.5154 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/25 05:00:00 | 23.5803 | 25.3076 | 24.3552 | 23.7799 | 23.5369 | 24.1336 | 24.679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.2072 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/25 06:00:00 | 23.4262 | 25.133 | 24.1898 | 23.6164 | 23.3682 | 23.9622 | 24.3466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.8471 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/25 07:00:00 | 23.1678 | 24.854 | 23.914 | 23.3418 | 23.0851 | 23.6768 | 24.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.78363 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/25 08:00:00 | 22.8894 | 24.5552 | 23.619 | 23.0467 | 22.7811 | 23.3706 | 23.7843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.8009 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/25 09:00:00 | 22.6828 | 24.2662 | 23.3994 | 22.7669 | 22.4935 | 23.0829 | 23.5364 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2115 | [14 empty] | 0.7285 |  | 4.8907 |  |  |  | 4.8907 |  | 4.8907 |  | 4.8907 |  | 4.8907 |  | 4.8907
02/25 10:00:00 | 22.5302 | 23.9813 | 23.2386 | 22.5559 | 22.2775 | 22.868 | 23.2993 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0004 | [14 empty] | 0.59147 |  | 9.0023 |  |  |  | 9.0023 |  | 9.0023 |  | 9.0023 |  | 9.0023 |  | 9.0023
02/25 11:00:00 | 22.271 | 23.6652 | 22.9683 | 22.3009 | 22.0165 | 22.6105 | 23.106 | 16.6354 | 22.4624 | 19.8863 | 18.5171 | 20.1812 | 13.9532 | 2.9339 | [14 empty] | 0.6972 |  | 187.7308 |  |  |  | 381.3649 |  | 287.3859 |  | 242.8363 |  | 297.4683 |  | 121.4263
02/25 12:00:00 | 22.099 | 23.5281 | 22.8238 | 22.1163 | 21.8368 | 22.3678 | 22.9949 | 13.5941 | 14.1287 | 13.8652 | 12.0206 | 12.9275 | 8.8667 | 2.8559 | [14 empty] | 0.80277 |  | 115.3086 |  |  |  | 127.0761 |  | 121.2049 |  | 83.9917 |  | 101.4374 |  | 36.1298
02/25 13:00:00 | 22.0127 | 23.477 | 22.7701 | 22.0102 | 21.7403 | 22.2219 | 22.8004 | 12.7266 | 12.4397 | 10.5148 | 10.667 | 16.5222 | 8.1571 | 2.8548 | [14 empty] | 0.6205 |  | 97.4531 |  |  |  | 91.8705 |  | 58.6758 |  | 61.0308 |  | 186.7989 |  | 28.115
02/25 14:00:00 | 21.971 | 23.4439 | 22.7109 | 21.9317 | 21.7165 | 22.1269 | 22.8155 | 15.1882 | 11.742 | 10.4681 | 12.7864 | 28.7363 | 10.0751 | 2.8056 | [14 empty] | 0.71324 |  | 153.3288 |  |  |  | 79.8595 |  | 58.715 |  | 99.6167 |  | 672.402 |  | 52.846
02/25 15:00:00 | 21.9697 | 23.4232 | 22.6851 | 21.9073 | 21.8977 | 22.0911 | 22.7947 | 22.4848 | 10.7098 | 11.4994 | 19.9348 | 33.1174 | 16.5195 | 2.8441 | [14 empty] | 0.68059 |  | 385.7601 |  |  |  | 61.8707 |  | 74.9148 |  | 292.0925 |  | 916.4748 |  | 187.017
02/25 16:00:00 | 22.1787 | 23.5158 | 22.7447 | 22.0252 | 22.7265 | 22.2055 | 22.7336 | 25.2871 | 9.7125 | 9.9819 | 27.1214 | 23.644 | 24.0396 | 2.8682 | [14 empty] | 0.30798 |  | 502.6052 |  |  |  | 46.8435 |  | 50.6044 |  | 588.217 |  | 431.6318 |  | 448.2283
02/25 17:00:00 | 22.4805 | 23.6091 | 22.7822 | 22.3261 | 23.4903 | 22.5165 | 22.3898 | 24.0389 | 8.22 | 8.2908 | 33.5349 | 20.704 | 32.9782 | 2.9884 | [14 empty] | 0.0082258 |  | 443.121 |  |  |  | 27.3699 |  | 28.1147 |  | 933.0856 |  | 313.8419 |  | 899.3865
02/25 18:00:00 | 22.6259 | 23.6186 | 22.7484 | 22.8693 | 23.6898 | 23.0817 | 21.888 | 30.3277 | 9.0567 | 9.3999 | 26.2048 | 19.4064 | 24.3614 | 33.2975 | [14 empty] | 0.54438 |  | 8.8196 |  |  |  | 587.6134 |  | 571.095 |  | 50.3067 |  | 192.9626 |  | 79.8537
02/25 19:00:00 | 22.8738 | 23.5285 | 22.6051 | 23.3704 | 23.665 | 23.6547 | 21.7702 | 29.3532 | 9.5517 | 13.0535 | 24.7336 | 20.713 | 22.5658 | 23.6457 | [14 empty] | 1.218 |  | 32.5751 |  |  |  | 198.6422 |  | 112.1948 |  | 1.1834 |  | 8.6007 |  | 1.1663
02/25 20:00:00 | 23.0556 | 23.2014 | 22.2744 | 23.3964 | 23.3414 | 23.7264 | 21.5925 | 23.5504 | 7.7381 | 11.6989 | 19.4747 | 16.4677 | 18.0673 | 8.44 | [14 empty] | 2.1406 |  | 228.3242 |  |  |  | 0.49276 |  | 10.6204 |  | 121.7641 |  | 64.4441 |  | 92.6836
02/25 21:00:00 | 22.9794 | 22.8449 | 22.0396 | 23.19 | 22.9455 | 23.4828 | 21.2018 | 22.6105 | 7.8228 | 10.1295 | 18.8866 | 15.9962 | 17.5954 | 18.3015 | [14 empty] | 3.1598 |  | 18.5673 |  |  |  | 109.804 |  | 66.7827 |  | 0.34225 |  | 5.3144 |  | 0.49857
02/25 22:00:00 | 22.8137 | 22.4915 | 21.7224 | 22.8731 | 22.5115 | 23.1339 | 20.9122 | 22.0689 | 7.804 | 10.3282 | 18.5972 | 15.8262 | 17.3502 | 19.6844 | [14 empty] | 3.6157 |  | 5.6862 |  |  |  | 141.1444 |  | 87.5391 |  | 1.1821 |  | 14.8853 |  | 5.4486
02/25 23:00:00 | 22.592 | 22.1108 | 21.4327 | 22.5429 | 22.053 | 22.7203 | 20.693 | 20.8401 | 7.7613 | 10.0754 | 17.6259 | 15.0925 | 16.4891 | 21.9121 | [14 empty] | 3.606 |  | 1.1493 |  |  |  | 200.2466 |  | 140.1082 |  | 18.372 |  | 46.5072 |  | 29.4088
02/25 24:00:00 | 22.326 | 21.7132 | 21.0978 | 22.1812 | 21.6655 | 22.3614 | 20.5339 | 19.945 | 7.6596 | 9.7814 | 16.9238 | 14.5514 | 15.8658 | 22.3023 | [14 empty] | 3.2119 |  | 5.5565 |  |  |  | 214.4078 |  | 156.7714 |  | 28.9274 |  | 60.0765 |  | 41.4274
02/26 01:00:00 | 22.043 | 21.3975 | 20.7827 | 21.8885 | 21.288 | 22.0121 | 20.3547 | 19.2033 | 7.5337 | 9.5775 | 16.3525 | 14.1026 | 15.3272 | 24.4855 | [14 empty] | 2.8505 |  | 27.9019 |  |  |  | 287.3648 |  | 222.2508 |  | 66.1468 |  | 107.8045 |  | 83.8748
02/26 02:00:00 | 21.7535 | 21.1116 | 20.501 | 21.6105 | 20.9863 | 21.7328 | 20.1913 | 18.5282 | 7.4351 | 9.3741 | 15.8156 | 13.6723 | 14.8681 | 25.1917 | [14 empty] | 2.4408 |  | 44.4018 |  |  |  | 315.2962 |  | 250.1948 |  | 87.9117 |  | 132.6956 |  | 106.5763
02/26 03:00:00 | 21.4552 | 20.8183 | 20.2148 | 21.3177 | 20.685 | 21.4564 | 20.0743 | 17.9235 | 7.3693 | 9.4124 | 15.3544 | 13.3259 | 14.4417 | 26.0374 | [14 empty] | 1.9069 |  | 65.8357 |  |  |  | 348.5006 |  | 276.393 |  | 114.1261 |  | 161.5835 |  | 134.4604
02/26 04:00:00 | 21.1492 | 20.5159 | 19.9215 | 21.0103 | 20.3661 | 21.1616 | 20.0004 | 17.0583 | 7.2379 | 25.8784 | 14.6482 | 12.7532 | 13.7881 | 26.4672 | [14 empty] | 1.3198 |  | 88.5274 |  |  |  | 369.7685 |  | 0.34679 |  | 139.6907 |  | 188.0741 |  | 160.7597
02/26 05:00:00 | 20.8481 | 20.2163 | 19.8009 | 20.7039 | 20.0476 | 20.864 | 19.9485 | 16.914 | 7.1846 | 39.3772 | 14.5389 | 12.7423 | 13.7189 | 26.8978 | [14 empty] | 0.80924 |  | 99.676 |  |  |  | 388.609 |  | 155.7361 |  | 152.7418 |  | 200.378 |  | 173.6832
02/26 06:00:00 | 20.5479 | 19.9162 | 20.0885 | 20.393 | 19.724 | 20.5597 | 19.9127 | 15.9021 | 26.3197 | 31.9029 | 13.7125 | 32.05 | 12.9302 | 27.65 | [14 empty] | 0.40348 |  | 138.0135 |  |  |  | 1.7697 |  | 18.0869 |  | 194.2522 |  | 19.3597 |  | 216.6715
02/26 07:00:00 | 20.2502 | 19.7644 | 20.4243 | 20.084 | 19.5647 | 20.2554 | 19.8939 | 15.4945 | 39.4204 | 27.6147 | 13.3898 | 45.2253 | 12.6204 | 28.207 | [14 empty] | 0.12701 |  | 161.607 |  |  |  | 125.7409 |  | 0.35079 |  | 219.5484 |  | 289.6229 |  | 242.9399
02/26 08:00:00 | 19.9568 | 19.986 | 20.5559 | 19.7781 | 19.7829 | 19.9452 | 19.8664 | 12.3466 | 38.6073 | 21.8923 | 11.3506 | 44.3325 | 10.8159 | 28.3071 | [14 empty] | 0.0081783 |  | 254.739 |  |  |  | 106.0936 |  | 41.1503 |  | 287.5235 |  | 256.8121 |  | 305.9426
02/26 09:00:00 | 19.7175 | 20.3409 | 20.5404 | 19.5406 | 20.1167 | 19.7082 | 20.2363 | 25.7423 | 53.4486 | 47.1823 | 29.4057 | 61.3568 | 41.2525 | 76.3487 | [14 empty] | 0.26915 |  | 2561.0024 |  |  |  | 524.4138 |  | 850.6766 |  | 2203.6414 |  | 224.7567 |  | 1231.744
02/26 10:00:00 | 19.6412 | 21.6504 | 20.7496 | 19.4894 | 21.5208 | 19.7519 | 21.3936 | 48.5916 | 43.5151 | 51.9879 | 59.7502 | 49.7807 | 59.3664 | 54.5491 | [14 empty] | 3.0709 |  | 35.492 |  |  |  | 121.7496 |  | 6.5596 |  | 27.0511 |  | 22.738 |  | 23.2061
02/26 11:00:00 | 19.8895 | 22.9746 | 21.6368 | 20.1175 | 22.6194 | 20.5268 | 22.0346 | 50.2936 | 38.5438 | 44.6779 | 57.2437 | 43.4213 | 57.2373 | 20.5518 | [14 empty] | 4.6013 |  | 884.5769 |  |  |  | 323.7117 |  | 582.0704 |  | 1346.2961 |  | 523.0136 |  | 1345.8251
02/26 12:00:00 | 20.2953 | 23.5093 | 22.6817 | 21.5369 | 22.9924 | 22.019 | 21.9861 | 51.0116 | 35.9372 | 39.8916 | 47.8686 | 40.4273 | 46.9819 | 27.9465 | [14 empty] | 2.8586 |  | 532.0031 |  |  |  | 63.8514 |  | 142.6861 |  | 396.8904 |  | 155.7727 |  | 362.3494
02/26 13:00:00 | 20.8196 | 23.7814 | 23.0396 | 22.7546 | 23.1175 | 23.2331 | 22.118 | 50.6799 | 33.3014 | 36.8343 | 41.8704 | 37.4356 | 41.2261 | 17.4802 | [14 empty] | 1.6857 |  | 1102.2176 |  |  |  | 250.3107 |  | 374.5796 |  | 594.8804 |  | 398.2185 |  | 563.8689
02/26 14:00:00 | 21.4421 | 23.9704 | 23.1691 | 23.2265 | 23.2188 | 23.7271 | 22.1755 | 45.1614 | 30.3396 | 33.6324 | 38.0606 | 34.0253 | 37.4016 | 3.5873 | [14 empty] | 0.5379 |  | 1728.4023 |  |  |  | 715.6872 |  | 902.7095 |  | 1188.408 |  | 926.474 |  | 1143.4072
02/26 15:00:00 | 22.2163 | 24.2662 | 23.3754 | 23.48 | 23.395 | 24.0591 | 22.0852 | 39.637 | 27.3518 | 30.0768 | 33.6737 | 29.9198 | 32.8734 | 8.4295 | [14 empty] | 0.017192 |  | 973.907 |  |  |  | 358.054 |  | 468.6084 |  | 637.2737 |  | 461.833 |  | 597.5073
02/26 16:00:00 | 22.9036 | 24.6809 | 23.6909 | 23.8159 | 23.6877 | 24.4953 | 22.1676 | 35.5692 | 23.7531 | 26.8267 | 29.785 | 26.3525 | 28.0867 | 6.9554 | [14 empty] | 0.54163 |  | 818.7524 |  |  |  | 282.1637 |  | 394.8682 |  | 521.1895 |  | 376.2472 |  | 446.5314
02/26 17:00:00 | 23.3763 | 25.1294 | 24.078 | 24.1928 | 24.0519 | 24.9373 | 22.2192 | 32.845 | 21.3316 | 24.7112 | 27.0954 | 24.079 | 25.1864 | 15.9738 | [14 empty] | 1.3387 |  | 284.6376 |  |  |  | 28.7062 |  | 76.3411 |  | 123.6894 |  | 65.6945 |  | 84.8715
02/26 18:00:00 | 23.6739 | 25.4705 | 24.3985 | 24.483 | 24.3414 | 25.2478 | 22.2653 | 30.7245 | 19.7063 | 23.0718 | 24.9801 | 22.3678 | 23.3664 | 18.5771 | [14 empty] | 1.9841 |  | 147.5591 |  |  |  | 1.2752 |  | 20.202 |  | 40.998 |  | 14.3691 |  | 22.9378
02/26 19:00:00 | 23.8893 | 25.7205 | 24.6328 | 24.6967 | 24.5621 | 25.4718 | 21.9945 | 31.9257 | 21.4197 | 23.945 | 26.5916 | 23.9574 | 26.696 | 25.0942 | [14 empty] | 3.5901 |  | 46.6696 |  |  |  | 13.5018 |  | 1.3206 |  | 2.2422 |  | 1.2923 |  | 2.5659
02/26 20:00:00 | 23.8645 | 25.6256 | 24.6056 | 24.5963 | 24.4579 | 25.3364 | 21.8029 | 26.1562 | 16.3891 | 18.7415 | 21.0434 | 19.0581 | 20.9947 | 9.9259 | [14 empty] | 4.2502 |  | 263.4219 |  |  |  | 41.772 |  | 77.7132 |  | 123.5974 |  | 83.3957 |  | 122.5165
02/26 21:00:00 | 23.6771 | 25.3442 | 24.4029 | 24.2772 | 24.0888 | 25.0405 | 21.4194 | 24.9686 | 16.0971 | 18.0974 | 20.2634 | 18.4061 | 20.1087 | 17.9286 | [14 empty] | 5.0969 |  | 49.5619 |  |  |  | 3.3543 |  | 0.02851 |  | 5.4512 |  | 0.22801 |  | 4.7529
02/26 22:00:00 | 23.4998 | 25.027 | 24.217 | 23.9408 | 23.6371 | 24.6734 | 21.1619 | 23.8782 | 15.6795 | 17.4416 | 19.4882 | 17.7673 | 19.3581 | 20.653 | [14 empty] | 5.4661 |  | 10.4019 |  |  |  | 24.7361 |  | 10.3133 |  | 1.3568 |  | 8.3275 |  | 1.6769
02/26 23:00:00 | 23.3013 | 24.7296 | 24.0216 | 23.5666 | 23.1779 | 24.2262 | 20.9229 | 22.643 | 15.155 | 16.7044 | 18.548 | 16.9858 | 18.4652 | 20.5255 | [14 empty] | 5.6571 |  | 4.4838 |  |  |  | 28.8426 |  | 14.6009 |  | 3.9105 |  | 12.5294 |  | 4.2451
02/26 24:00:00 | 23.0876 | 24.4264 | 23.8102 | 23.189 | 22.7944 | 23.8542 | 20.6663 | 22.1185 | 14.746 | 16.3311 | 18.29 | 16.7901 | 18.2182 | 23.3265 | [14 empty] | 5.863 |  | 1.4593 |  |  |  | 73.6246 |  | 48.9356 |  | 25.3664 |  | 42.7253 |  | 26.0948
02/27 01:00:00 | 22.8534 | 24.1642 | 23.5793 | 22.8662 | 22.4517 | 23.5214 | 20.5451 | 20.5802 | 14.1894 | 15.4279 | 17.0157 | 15.6358 | 16.9609 | 23.7857 | [14 empty] | 5.3281 |  | 10.2755 |  |  |  | 92.0892 |  | 69.8526 |  | 45.8327 |  | 66.4218 |  | 46.5782
02/27 02:00:00 | 22.6472 | 23.9474 | 23.3773 | 22.5811 | 22.1452 | 23.2281 | 20.4837 | 19.8622 | 13.6567 | 14.9206 | 16.5061 | 15.207 | 16.4425 | 22.9996 | [14 empty] | 4.6808 |  | 9.8429 |  |  |  | 87.2887 |  | 65.2692 |  | 42.1646 |  | 60.7239 |  | 42.9943
02/27 03:00:00 | 22.4326 | 23.7182 | 23.1703 | 22.3531 | 21.8984 | 22.9918 | 20.4639 | 15.7915 | 13.304 | 14.438 | 15.959 | 14.7295 | 15.9071 | 23.1668 | [14 empty] | 3.8757 |  | 54.3938 |  |  |  | 97.2744 |  | 76.1917 |  | 51.9524 |  | 71.1867 |  | 52.7032
02/27 04:00:00 | 22.2318 | 23.4808 | 22.9538 | 22.1207 | 21.6495 | 22.7514 | 20.5138 | 15.4327 | 12.8384 | 13.919 | 15.3395 | 14.1834 | 15.2972 | 22.4324 | [14 empty] | 2.9516 |  | 48.9963 |  |  |  | 92.0446 |  | 72.4792 |  | 50.3092 |  | 68.0459 |  | 50.912
02/27 05:00:00 | 22.0819 | 23.2439 | 22.7449 | 21.8847 | 21.3988 | 22.5077 | 20.4808 | 15.1974 | 12.4717 | 11.3052 | 14.9275 | 13.791 | 14.8829 | 23.3754 | [14 empty] | 2.5636 |  | 66.8804 |  |  |  | 118.8917 |  | 145.6901 |  | 71.3676 |  | 91.8621 |  | 72.1227
02/27 06:00:00 | 21.9307 | 23.0103 | 22.569 | 21.6473 | 21.146 | 22.2623 | 20.4687 | 14.425 | 12.0425 | 11.0922 | 14.1347 | 13.119 | 14.0952 | 23.2557 | [14 empty] | 2.1374 |  | 77.9816 |  |  |  | 125.7355 |  | 147.9515 |  | 83.1927 |  | 102.7524 |  | 83.9156
02/27 07:00:00 | 21.7777 | 22.7817 | 22.4374 | 21.4107 | 20.8965 | 22.0185 | 20.5016 | 13.9397 | 11.5783 | 10.7777 | 13.5701 | 12.5814 | 13.5389 | 22.3393 | [14 empty] | 1.6285 |  | 70.5527 |  |  |  | 115.7987 |  | 133.6703 |  | 76.8974 |  | 95.2165 |  | 77.4462
02/27 08:00:00 | 21.6241 | 22.5436 | 22.304 | 21.1781 | 20.6421 | 21.7796 | 20.9057 | 16.7285 | 13.2584 | 13.6108 | 14.7684 | 14.2277 | 14.9406 | 76.04 | [14 empty] | 0.51614 |  | 3517.8473 |  |  |  | 3941.5294 |  | 3897.4069 |  | 3754.2057 |  | 3820.7533 |  | 3733.1358
02/27 09:00:00 | 21.4934 | 22.3806 | 22.1922 | 21.0165 | 20.4804 | 21.6155 | 21.994 | 19.846 | 14.4609 | 15.1677 | 43.5372 | 46.2432 | 17.5123 | 16.6703 | [14 empty] | 0.25055 |  | 10.0849 |  |  |  | 4.8816 |  | 2.2577 |  | 721.8297 |  | 874.5548 |  | 0.70904
02/27 10:00:00 | 21.4727 | 22.3696 | 22.1865 | 21.2813 | 20.7664 | 21.5979 | 22.1355 | 26.6268 | 13.2363 | 18.0587 | 43.5538 | 58.7769 | 32.1512 | 15.7638 | [14 empty] | 0.43933 |  | 118.0049 |  |  |  | 6.388 |  | 5.2667 |  | 772.2865 |  | 1850.1305 |  | 268.5469
02/27 11:00:00 | 21.6879 | 22.5102 | 22.3758 | 22.718 | 22.5616 | 21.9348 | 22.1332 | 32.5322 | 12.0478 | 16.9437 | 32.0913 | 38.7474 | 37.8 | 14.6812 | [14 empty] | 0.19834 |  | 318.6594 |  |  |  | 6.9346 |  | 5.119 |  | 303.113 |  | 579.1834 |  | 534.48
02/27 12:00:00 | 22.2574 | 22.7558 | 22.815 | 23.9334 | 24.6536 | 23.0367 | 22.1409 | 26.6456 | 10.733 | 13.6498 | 27.5625 | 31.682 | 26.9749 | 14.6984 | [14 empty] | 0.013579 |  | 142.7352 |  |  |  | 15.7249 |  | 1.0996 |  | 165.4848 |  | 288.4404 |  | 150.7122
02/27 13:00:00 | 22.9732 | 23.0618 | 23.2459 | 24.4083 | 25.4043 | 24.3113 | 22.3326 | 24.0466 | 9.8081 | 12.9915 | 26.2391 | 31.131 | 23.3139 | 8.8859 | [14 empty] | 0.41046 |  | 229.8451 |  |  |  | 0.8504 |  | 16.8555 |  | 301.1323 |  | 494.8449 |  | 208.1678
02/27 14:00:00 | 23.1881 | 23.1343 | 23.3012 | 24.4719 | 25.4061 | 24.5625 | 22.4608 | 21.3289 | 8.5306 | 11.2358 | 23.0371 | 26.9464 | 20.625 | 3.2098 | [14 empty] | 0.52909 |  | 328.3006 |  |  |  | 28.31 |  | 64.4156 |  | 393.1188 |  | 563.4242 |  | 303.2862
02/27 15:00:00 | 23.4943 | 23.3918 | 23.5057 | 24.6635 | 25.5946 | 24.8322 | 22.334 | 20.2857 | 7.7345 | 10.528 | 21.79 | 25.5955 | 19.6506 | 23.408 | [14 empty] | 1.3463 |  | 9.7488 |  |  |  | 245.6571 |  | 165.8955 |  | 2.6181 |  | 4.7854 |  | 14.1178
02/27 16:00:00 | 23.9185 | 23.8435 | 23.9059 | 25.023 | 25.94 | 25.232 | 22.5398 | 19.0503 | 7.1978 | 9.8501 | 20.3864 | 23.931 | 18.3518 | 9.8294 | [14 empty] | 1.9007 |  | 85.0242 |  |  |  | 6.9254 |  | 0.00042747 |  | 111.4498 |  | 198.8528 |  | 72.6304
02/27 17:00:00 | 24.1718 | 24.1526 | 24.184 | 25.2115 | 26.1561 | 25.4746 | 22.3176 | 19.2042 | 7.1243 | 10.1015 | 20.3635 | 24.1449 | 18.4393 | 5.849 | [14 empty] | 3.438 |  | 178.363 |  |  |  | 1.6265 |  | 18.0841 |  | 210.6698 |  | 334.7417 |  | 158.5159
02/27 18:00:00 | 24.1326 | 24.1295 | 24.1366 | 25.1402 | 26.1003 | 25.3979 | 22.0847 | 18.518 | 7.3742 | 10.1388 | 19.4696 | 22.7903 | 17.7088 | 14.878 | [14 empty] | 4.1938 |  | 13.2496 |  |  |  | 56.3068 |  | 22.4594 |  | 21.0827 |  | 62.6052 |  | 8.0136
02/27 19:00:00 | 23.8894 | 23.8526 | 23.8629 | 24.8852 | 25.8333 | 25.0965 | 22.0511 | 17.6191 | 7.4892 | 9.9089 | 18.439 | 21.4271 | 16.8746 | 17.9146 | [14 empty] | 3.3791 |  | 0.087349 |  |  |  | 108.6891 |  | 64.0922 |  | 0.27493 |  | 12.3374 |  | 1.0817
02/27 20:00:00 | 23.4421 | 23.3648 | 23.3907 | 24.437 | 25.2971 | 24.6263 | 22.1003 | 16.8468 | 7.3896 | 9.6158 | 17.5589 | 20.4385 | 16.1524 | 17.8393 | [14 empty] | 1.8004 |  | 0.98515 |  |  |  | 109.1957 |  | 67.6268 |  | 0.078639 |  | 6.7557 |  | 2.8456
02/27 21:00:00 | 23.061 | 22.9601 | 22.9901 | 24.0536 | 24.8301 | 24.1613 | 21.911 | 13.9701 | 5.7831 | 7.7305 | 14.0004 | 16.1329 | 12.9584 | 9.306 | [14 empty] | 1.3224 |  | 21.7542 |  |  |  | 12.4106 |  | 2.4823 |  | 22.0377 |  | 46.6067 |  | 13.34
02/27 22:00:00 | 22.7449 | 22.6215 | 22.6626 | 23.727 | 24.4124 | 23.8198 | 21.6902 | 11.3744 | 5.7971 | 7.6182 | 13.6293 | 15.6601 | 12.6318 | 14.2341 | [14 empty] | 1.1124 |  | 8.1774 |  |  |  | 71.1825 |  | 43.7691 |  | 0.36578 |  | 2.0337 |  | 2.5673
02/27 23:00:00 | 22.5061 | 22.3057 | 22.3685 | 23.4237 | 23.9909 | 23.5277 | 21.5534 | 13.4019 | 5.7422 | 7.4714 | 13.1578 | 15.1759 | 12.1964 | 14.5634 | [14 empty] | 0.90761 |  | 1.349 |  |  |  | 77.8137 |  | 50.296 |  | 1.9757 |  | 0.37513 |  | 5.6027
02/27 24:00:00 | 22.2994 | 22.0072 | 22.0962 | 23.1327 | 23.6052 | 23.2367 | 21.4713 | 12.5576 | 5.6196 | 7.2216 | 12.5598 | 14.4892 | 11.6487 | 15.4236 | [14 empty] | 0.68581 |  | 8.2139 |  |  |  | 96.1187 |  | 67.2716 |  | 8.2011 |  | 0.87314 |  | 14.2497
02/28 01:00:00 | 22.025 | 21.7228 | 21.8393 | 22.8537 | 23.2578 | 22.9575 | 21.3886 | 9.9458 | 5.4979 | 6.9467 | 11.918 | 13.7629 | 11.0805 | 16.0665 | [14 empty] | 0.40494 |  | 37.4622 |  |  |  | 111.6938 |  | 83.1707 |  | 17.2098 |  | 5.3064 |  | 24.8593
02/28 02:00:00 | 21.8318 | 21.4776 | 21.6262 | 22.6044 | 23.0153 | 22.7163 | 21.4066 | 9.55 | 5.3119 | 6.6728 | 11.3468 | 13.0741 | 10.5217 | 15.1034 | [14 empty] | 0.1808 |  | 30.8397 |  |  |  | 95.8724 |  | 71.0746 |  | 14.1116 |  | 4.1178 |  | 20.9919
02/28 03:00:00 | 21.684 | 21.2367 | 21.4187 | 22.3699 | 22.7871 | 22.4775 | 21.5201 | 9.2681 | 4.4343 | 5.4869 | 10.8557 | 12.5083 | 10.1267 | 14.6168 | [14 empty] | 0.026848 |  | 28.6086 |  |  |  | 103.6841 |  | 83.3561 |  | 14.1464 |  | 4.446 |  | 20.1609
02/28 04:00:00 | 21.5453 | 21.0671 | 21.2609 | 22.135 | 22.5636 | 22.2553 | 21.4232 | 9.0049 | 4.4088 | 5.468 | 9.2703 | 12.0712 | 8.7442 | 16.0661 | [14 empty] | 0.014918 |  | 49.8609 |  |  |  | 135.8935 |  | 112.3203 |  | 46.1827 |  | 15.9591 |  | 53.61
02/28 05:00:00 | 21.404 | 20.948 | 21.1469 | 21.9538 | 22.3375 | 22.0831 | 21.3101 | 10.2682 | 4.9719 | 6.1378 | 10.0696 | 11.2889 | 9.3814 | 16.3467 | [14 empty] | 0.0088157 |  | 36.9487 |  |  |  | 129.3869 |  | 104.2221 |  | 39.402 |  | 25.5815 |  | 48.5153
02/28 06:00:00 | 21.217 | 20.7751 | 20.9912 | 21.7692 | 22.0946 | 21.9064 | 21.2046 | 9.8032 | 4.7597 | 5.8998 | 9.6384 | 10.9322 | 8.9905 | 17.3812 | [14 empty] | 0.00015465 |  | 57.4252 |  |  |  | 159.3009 |  | 131.8223 |  | 59.9507 |  | 41.5884 |  | 70.4023
02/28 07:00:00 | 20.9435 | 20.5279 | 20.7498 | 21.4935 | 21.8012 | 21.6401 | 21.0952 | 9.5872 | 4.7255 | 5.8578 | 9.4422 | 10.7699 | 8.8203 | 18.4105 | [14 empty] | 0.023005 |  | 77.8505 |  |  |  | 187.2799 |  | 157.5724 |  | 80.4319 |  | 58.3797 |  | 91.9732
02/28 08:00:00 | 20.6683 | 20.2766 | 20.5025 | 21.2087 | 21.5136 | 21.3639 | 21.4382 | 10.4102 | 5.575 | 6.6957 | 10.824 | 14.2619 | 12.1356 | 49.5013 | [14 empty] | 0.59264 |  | 1528.1102 |  |  |  | 1929.5218 |  | 1832.3211 |  | 1495.9364 |  | 1241.8142 |  | 1396.1951
02/28 09:00:00 | 20.4622 | 20.0965 | 20.3271 | 20.9971 | 21.2239 | 21.1108 | 22.1531 | 32.1049 | 36.2887 | 34.4321 | 38.4176 | 25.7633 | 40.3188 | 7.9799 | [14 empty] | 2.859 |  | 582.0127 |  |  |  | 801.3853 |  | 699.7182 |  | 926.4506 |  | 316.2466 |  | 1045.7999
02/28 10:00:00 | 20.7565 | 20.416 | 20.7272 | 21.2436 | 21.3193 | 21.3815 | 22.295 | 44.9295 | 50.8898 | 47.1332 | 39.5632 | 36.0527 | 39.7541 | 5.1046 | [14 empty] | 2.367 |  | 1586.026 |  |  |  | 2096.2858 |  | 1766.4053 |  | 1187.3988 |  | 957.788 |  | 1200.5867
02/28 11:00:00 | 21.8684 | 22.339 | 22.2427 | 22.9146 | 22.4434 | 23.4181 | 22.5371 | 34.6357 | 30.4638 | 33.3482 | 27.1844 | 24.0895 | 26.571 | 3.1222 | [14 empty] | 0.4471 |  | 993.0956 |  |  |  | 747.5587 |  | 913.6063 |  | 578.9861 |  | 439.6241 |  | 549.8449
02/28 12:00:00 | 23.3794 | 25.0829 | 24.4261 | 24.3828 | 23.842 | 25.0352 | 22.7667 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8669 | [14 empty] | 0.37534 |  | 8.2194 |  |  |  | 8.2194 |  | 8.2194 |  | 8.2194 |  | 8.2194 |  | 8.2194
02/28 13:00:00 | 23.6244 | 26.1214 | 24.9768 | 24.6728 | 24.3809 | 25.3151 | 22.745 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7792 | [14 empty] | 0.77329 |  | 7.7238 |  |  |  | 7.7238 |  | 7.7238 |  | 7.7238 |  | 7.7238 |  | 7.7238
02/28 14:00:00 | 23.2142 | 25.776 | 24.592 | 24.3851 | 24.1979 | 25.034 | 22.7817 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6567 | [14 empty] | 0.18705 |  | 7.0582 |  |  |  | 7.0582 |  | 7.0582 |  | 7.0582 |  | 7.0582 |  | 7.0582
02/28 15:00:00 | 22.9878 | 25.5346 | 24.3683 | 24.1731 | 24.006 | 24.8192 | 22.7811 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6591 | [14 empty] | 0.042732 |  | 7.0708 |  |  |  | 7.0708 |  | 7.0708 |  | 7.0708 |  | 7.0708 |  | 7.0708
02/28 16:00:00 | 23.1021 | 25.6016 | 24.4992 | 24.2797 | 24.1236 | 24.9194 | 22.8569 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7011 | [14 empty] | 0.060114 |  | 7.2962 |  |  |  | 7.2962 |  | 7.2962 |  | 7.2962 |  | 7.2962 |  | 7.2962
02/28 17:00:00 | 23.1858 | 25.6592 | 24.6053 | 24.3508 | 24.1968 | 24.9859 | 22.964 | 0 | 0 | 0 | 0 | 0 | 0 | 17.0978 | [14 empty] | 0.049219 |  | 292.3345 |  |  |  | 292.3345 |  | 292.3345 |  | 292.3345 |  | 292.3345 |  | 292.3345
02/28 18:00:00 | 23.1005 | 25.5768 | 24.5477 | 24.2641 | 24.0963 | 24.8961 | 23.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2102 | [14 empty] | 0.0016211 |  | 10.3052 |  |  |  | 10.3052 |  | 10.3052 |  | 10.3052 |  | 10.3052 |  | 10.3052
02/28 19:00:00 | 22.9423 | 25.4122 | 24.4064 | 24.0941 | 23.9179 | 24.7203 | 22.8863 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8295 | [14 empty] | 0.0031383 |  | 8.0059 |  |  |  | 8.0059 |  | 8.0059 |  | 8.0059 |  | 8.0059 |  | 8.0059
02/28 20:00:00 | 22.5475 | 25.0225 | 24.0403 | 23.6999 | 23.5059 | 24.3147 | 22.5767 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8631 | [14 empty] | 0.00085321 |  | 8.1972 |  |  |  | 8.1972 |  | 8.1972 |  | 8.1972 |  | 8.1972 |  | 8.1972
02/28 21:00:00 | 22.1569 | 24.5334 | 23.6811 | 23.3114 | 23.0973 | 23.9107 | 22.3776 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5704 | [14 empty] | 0.048738 |  | 43.1707 |  |  |  | 43.1707 |  | 43.1707 |  | 43.1707 |  | 43.1707 |  | 43.1707
02/28 22:00:00 | 21.9171 | 24.1802 | 23.4619 | 23.0129 | 22.7797 | 23.595 | 22.2422 | 0 | 0 | 0 | 0 | 0 | 0 | 2.833 | [14 empty] | 0.10567 |  | 8.0261 |  |  |  | 8.0261 |  | 8.0261 |  | 8.0261 |  | 8.0261 |  | 8.0261
02/28 23:00:00 | 21.7659 | 23.8949 | 23.3234 | 22.8043 | 22.4948 | 23.3111 | 22.0917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.10613 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
02/28 24:00:00 | 21.5865 | 23.6464 | 23.1625 | 22.6333 | 22.2548 | 23.0709 | 21.9493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.13163 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 01:00:00 | 21.4126 | 23.4218 | 23.0081 | 22.4644 | 22.0902 | 22.9055 | 21.8508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.19204 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 02:00:00 | 21.334 | 23.2891 | 22.9442 | 22.3854 | 22.0121 | 22.8261 | 21.8299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.24597 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 03:00:00 | 21.2606 | 23.2054 | 22.8869 | 22.3101 | 21.9349 | 22.7468 | 21.7629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.25232 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 04:00:00 | 21.2061 | 23.1371 | 22.8481 | 22.2532 | 21.8751 | 22.6846 | 21.7331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.27773 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 05:00:00 | 21.1608 | 23.0732 | 22.8169 | 22.2054 | 21.8216 | 22.6283 | 21.7198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.31251 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 06:00:00 | 21.1168 | 23.0106 | 22.7868 | 22.1578 | 21.7705 | 22.5746 | 21.6333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.26678 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 07:00:00 | 21.0685 | 22.944 | 22.7517 | 22.1051 | 21.7128 | 22.5144 | 21.5292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.21221 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 08:00:00 | 21.0161 | 22.8744 | 22.7116 | 22.0474 | 21.65 | 22.4494 | 21.3642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.12115 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 09:00:00 | 20.9872 | 22.8271 | 22.6948 | 22.0124 | 21.61 | 22.4066 | 21.3154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.10776 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 10:00:00 | 21.0917 | 22.8759 | 22.8209 | 22.1019 | 21.6925 | 22.4822 | 21.3437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.063497 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 11:00:00 | 21.4036 | 23.0622 | 23.1555 | 22.3314 | 21.9167 | 22.6964 | 21.3373 | 0 | 0 | 0 | 0 | 0 | 0 | 29.796 | [14 empty] | 0.0044028 |  | 887.8034 |  |  |  | 887.8034 |  | 887.8034 |  | 887.8034 |  | 887.8034 |  | 887.8034
03/01 12:00:00 | 21.6699 | 23.2796 | 23.4265 | 22.5514 | 22.1349 | 22.9063 | 21.6868 | 0 | 0 | 0 | 0 | 0 | 0 | 15.1551 | [14 empty] | 0.00028693 |  | 229.6777 |  |  |  | 229.6777 |  | 229.6777 |  | 229.6777 |  | 229.6777 |  | 229.6777
03/01 13:00:00 | 21.7967 | 23.4069 | 23.5537 | 22.6638 | 22.2463 | 23.0126 | 21.9797 | 0 | 0 | 0 | 0 | 0 | 0 | 14.8786 | [14 empty] | 0.033499 |  | 221.373 |  |  |  | 221.373 |  | 221.373 |  | 221.373 |  | 221.373 |  | 221.373
03/01 14:00:00 | 21.665 | 23.3038 | 23.4216 | 22.5301 | 22.1067 | 22.8747 | 22.2936 | 0 | 0 | 0 | 0 | 0 | 0 | 6.943 | [14 empty] | 0.3951 |  | 48.2054 |  |  |  | 48.2054 |  | 48.2054 |  | 48.2054 |  | 48.2054 |  | 48.2054
03/01 15:00:00 | 21.6734 | 23.3499 | 23.4333 | 22.537 | 22.1069 | 22.8815 | 22.6866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.0265 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 16:00:00 | 22.1024 | 23.7953 | 23.8694 | 22.961 | 22.5328 | 23.3172 | 22.853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.56337 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 17:00:00 | 22.8729 | 24.7587 | 24.6864 | 23.7359 | 23.3856 | 24.2138 | 22.7845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.0078232 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 18:00:00 | 23.1535 | 25.1681 | 24.9689 | 24.0099 | 23.6616 | 24.5117 | 22.9133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.057699 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 19:00:00 | 23.09 | 25.1029 | 24.9103 | 23.9489 | 23.577 | 24.4175 | 22.7531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.11353 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/01 20:00:00 | 22.8309 | 24.8434 | 24.6539 | 23.6918 | 23.3079 | 24.1349 | 22.4149 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9396 | [14 empty] | 0.17304 |  | 48.1585 |  |  |  | 48.1585 |  | 48.1585 |  | 48.1585 |  | 48.1585 |  | 48.1585
03/01 21:00:00 | 22.4989 | 24.4663 | 24.326 | 23.3601 | 22.962 | 23.7409 | 22.2399 | 0 | 0 | 0 | 0 | 0 | 0 | 3.657 | [14 empty] | 0.067072 |  | 13.3738 |  |  |  | 13.3738 |  | 13.3738 |  | 13.3738 |  | 13.3738 |  | 13.3738
03/01 22:00:00 | 22.1578 | 24.0016 | 23.9896 | 23.0156 | 22.5464 | 23.2665 | 21.8723 | 0 | 0 | 0 | 0 | 0 | 0 | 3.206 | [14 empty] | 0.081515 |  | 10.2786 |  |  |  | 10.2786 |  | 10.2786 |  | 10.2786 |  | 10.2786 |  | 10.2786
03/01 23:00:00 | 21.7611 | 23.5486 | 23.6452 | 22.6085 | 22.1372 | 22.8129 | 21.4084 | 35.803 | 35.3041 | 33.975 | 32.5667 | 29.9508 | 33.4477 | 3.0354 | [14 empty] | 0.1244 |  | 1073.7173 |  |  |  | 1041.2709 |  | 957.2584 |  | 872.0958 |  | 724.4379 |  | 924.9087
03/01 24:00:00 | 21.9487 | 23.5897 | 23.8513 | 22.5907 | 22.0774 | 22.8303 | 20.9356 | 27.8265 | 22.0429 | 24.0518 | 22.0239 | 19.0262 | 21.9611 | 3.0159 | [14 empty] | 1.0265 |  | 615.5691 |  |  |  | 362.0277 |  | 442.5111 |  | 361.3059 |  | 256.3312 |  | 358.9216
03/02 01:00:00 | 22.2266 | 23.7121 | 24.0356 | 22.6491 | 22.0539 | 22.9069 | 20.4484 | 26.3485 | 20.3142 | 22.6333 | 20.6872 | 17.7906 | 20.5375 | 2.8275 | [14 empty] | 3.1623 |  | 553.2358 |  |  |  | 305.7855 |  | 392.2673 |  | 318.9697 |  | 223.8929 |  | 313.6449
03/02 02:00:00 | 22.3696 | 23.786 | 24.1102 | 22.6552 | 21.9884 | 22.9228 | 19.9999 | 25.0804 | 19.4886 | 21.6551 | 19.8146 | 17.1139 | 19.6627 | 2.8463 | [14 empty] | 5.6154 |  | 494.3567 |  |  |  | 276.9663 |  | 353.7744 |  | 287.9264 |  | 203.5668 |  | 282.7943
03/02 03:00:00 | 22.4152 | 23.7899 | 24.0926 | 22.5856 | 21.8602 | 22.8576 | 19.5089 | 23.9924 | 18.7384 | 20.7933 | 19.0678 | 16.5371 | 18.9264 | 10.8364 | [14 empty] | 8.4467 |  | 173.0805 |  |  |  | 62.4425 |  | 99.1405 |  | 67.7554 |  | 32.4979 |  | 65.4482
03/02 04:00:00 | 22.3957 | 23.7455 | 24.019 | 22.4681 | 21.6953 | 22.742 | 19.1866 | 24.5855 | 18.4406 | 20.8905 | 19.7379 | 17.2568 | 19.6 | 18.1965 | [14 empty] | 10.2981 |  | 40.8192 |  |  |  | 0.059597 |  | 7.2579 |  | 2.376 |  | 0.88299 |  | 1.9699
03/02 05:00:00 | 22.2277 | 23.5743 | 23.8009 | 22.2036 | 21.3849 | 22.4768 | 19.0364 | 23.0691 | 17.901 | 19.9711 | 18.6909 | 16.4171 | 18.568 | 17.4463 | [14 empty] | 10.1848 |  | 31.6157 |  |  |  | 0.20681 |  | 6.3746 |  | 1.5492 |  | 1.0591 |  | 1.2582
03/02 06:00:00 | 22.0351 | 23.3809 | 23.5698 | 21.9315 | 21.0761 | 22.202 | 18.8652 | 21.0755 | 17.0726 | 18.6431 | 17.0887 | 14.9894 | 16.9795 | 18.6761 | [14 empty] | 10.0484 |  | 5.757 |  |  |  | 2.5713 |  | 0.0010935 |  | 2.5199 |  | 13.5918 |  | 2.8787
03/02 07:00:00 | 21.8454 | 23.1939 | 23.3494 | 21.6826 | 20.803 | 21.953 | 18.7117 | 20.4599 | 16.4465 | 18.0308 | 16.6691 | 14.6811 | 16.5515 | 19.539 | [14 empty] | 9.8202 |  | 0.84794 |  |  |  | 9.5639 |  | 2.2749 |  | 8.2363 |  | 23.5992 |  | 8.9254
03/02 08:00:00 | 21.6197 | 22.976 | 23.1013 | 21.4095 | 20.5121 | 21.6795 | 18.8802 | 20.3523 | 21.5125 | 21.7874 | 21.3487 | 44.1384 | 21.4636 | 81.3724 | [14 empty] | 7.5052 |  | 3723.4595 |  |  |  | 3583.2047 |  | 3550.3769 |  | 3602.8417 |  | 1386.3744 |  | 3589.0676
03/02 09:00:00 | 21.4279 | 22.7737 | 22.8734 | 21.1625 | 20.4486 | 21.447 | 19.7262 | 24.6647 | 19.8249 | 20.6324 | 46.4587 | 61.6254 | 38.6799 | 50.6682 | [14 empty] | 2.8956 |  | 676.1802 |  |  |  | 951.3101 |  | 902.1504 |  | 17.7196 |  | 120.0604 |  | 143.7181
03/02 10:00:00 | 21.4047 | 22.6998 | 22.7866 | 21.3175 | 21.6908 | 21.5515 | 20.8106 | 34.9411 | 18.2832 | 18.9835 | 47.821 | 46.6016 | 45.2317 | 60.7688 | [14 empty] | 0.35305 |  | 667.0713 |  |  |  | 1805.0244 |  | 1746.0102 |  | 167.6443 |  | 200.709 |  | 241.4028
03/02 11:00:00 | 21.7473 | 22.8443 | 22.9091 | 22.8404 | 23.7993 | 22.7134 | 21.9063 | 39.1567 | 16.7752 | 17.6704 | 36.8727 | 39.2145 | 34.1962 | 10.9608 | [14 empty] | 0.025296 |  | 795.0108 |  |  |  | 33.8077 |  | 45.0183 |  | 671.425 |  | 798.2725 |  | 539.8848
03/02 12:00:00 | 22.5028 | 23.1981 | 23.1767 | 24.2402 | 24.8275 | 24.2356 | 22.2618 | 33.2456 | 15.3409 | 16.1906 | 32.2905 | 35.728 | 29.0131 | 22.4941 | [14 empty] | 0.058124 |  | 115.5945 |  |  |  | 51.1687 |  | 39.7343 |  | 95.9687 |  | 175.1362 |  | 42.4973
03/02 13:00:00 | 23.2597 | 23.6159 | 23.4642 | 24.7306 | 25.1876 | 24.7749 | 22.3933 | 29.3059 | 13.7257 | 14.549 | 29.6334 | 32.9107 | 26.6157 | 3.9826 | [14 empty] | 0.7507 |  | 641.2667 |  |  |  | 94.927 |  | 111.6489 |  | 657.9644 |  | 836.8337 |  | 512.2551
03/02 14:00:00 | 23.4206 | 23.7015 | 23.4186 | 24.701 | 25.2138 | 24.7972 | 22.3046 | 27.7365 | 12.7116 | 13.6526 | 27.6722 | 30.3191 | 24.9078 | 24.6083 | [14 empty] | 1.2456 |  | 9.7853 |  |  |  | 141.5322 |  | 120.0287 |  | 9.3875 |  | 32.6129 |  | 0.089681
03/02 15:00:00 | 23.5466 | 23.8372 | 23.4668 | 24.7644 | 25.3372 | 24.9206 | 22.2645 | 24.5105 | 11.612 | 12.1246 | 24.3766 | 26.7434 | 21.8902 | 21.2642 | [14 empty] | 1.6439 |  | 10.5384 |  |  |  | 93.1651 |  | 83.5323 |  | 9.6867 |  | 30.022 |  | 0.39191
03/02 16:00:00 | 23.8884 | 24.2188 | 23.8141 | 25.0805 | 25.6828 | 25.2766 | 22.2847 | 23.5376 | 10.9064 | 11.5983 | 23.2194 | 25.6029 | 20.9197 | 19.9246 | [14 empty] | 2.5719 |  | 13.0532 |  |  |  | 81.328 |  | 69.3285 |  | 10.8554 |  | 32.2426 |  | 0.99022
03/02 17:00:00 | 24.1619 | 24.5389 | 24.0926 | 25.3156 | 25.9203 | 25.5469 | 22.2248 | 23.555 | 10.997 | 12.0036 | 23.0322 | 25.5076 | 20.9298 | 29.8318 | [14 empty] | 3.7526 |  | 39.3979 |  |  |  | 354.7488 |  | 317.8432 |  | 46.2343 |  | 18.6984 |  | 79.2443
03/02 18:00:00 | 24.0843 | 24.5309 | 24.0284 | 25.1808 | 25.8067 | 25.4317 | 22.2119 | 22.3759 | 10.7383 | 11.5126 | 21.8982 | 24.1035 | 19.902 | 27.6981 | [14 empty] | 3.5061 |  | 28.3262 |  |  |  | 287.6356 |  | 261.9721 |  | 33.6388 |  | 12.9215 |  | 60.7796
03/02 19:00:00 | 23.8898 | 24.3566 | 23.8097 | 24.954 | 25.5534 | 25.2163 | 22.1118 | 21.7709 | 10.6017 | 11.6171 | 21.1054 | 23.1057 | 19.2939 | 30.4868 | [14 empty] | 3.1615 |  | 75.9671 |  |  |  | 395.4173 |  | 356.0655 |  | 88.0093 |  | 54.4799 |  | 125.2807
03/02 20:00:00 | 23.4457 | 23.85 | 23.3313 | 24.4271 | 24.9889 | 24.6896 | 21.9379 | 21.2987 | 10.7724 | 11.6061 | 20.5908 | 22.4655 | 18.9151 | 32.563 | [14 empty] | 2.2734 |  | 126.8838 |  |  |  | 474.8292 |  | 439.1895 |  | 143.3316 |  | 101.9589 |  | 186.2637
03/02 21:00:00 | 22.893 | 23.2544 | 22.733 | 23.8501 | 24.4088 | 24.1064 | 21.6687 | 17.8848 | 8.4405 | 9.6797 | 16.8316 | 18.1776 | 15.6088 | 4.672 | [14 empty] | 1.4988 |  | 174.5793 |  |  |  | 14.2016 |  | 25.0772 |  | 147.8562 |  | 182.4035 |  | 119.6151
03/02 22:00:00 | 22.4607 | 22.6981 | 22.1652 | 23.2989 | 23.8022 | 23.5432 | 20.939 | 16.9313 | 8.3445 | 9.3911 | 16.0025 | 17.3114 | 14.8603 | 3.5299 | [14 empty] | 2.3154 |  | 179.5978 |  |  |  | 23.1803 |  | 34.3547 |  | 155.566 |  | 189.93 |  | 128.3787
03/02 23:00:00 | 22.0722 | 22.2704 | 21.7503 | 22.7742 | 23.126 | 23.0067 | 20.1335 | 15.9247 | 8.1405 | 9.037 | 15.0372 | 16.2958 | 13.9792 | 3.2403 | [14 empty] | 3.7586 |  | 160.8936 |  |  |  | 24.0125 |  | 33.6019 |  | 139.1664 |  | 170.4473 |  | 115.3243
03/02 24:00:00 | 21.6393 | 21.8306 | 21.3301 | 22.2733 | 22.5078 | 22.5 | 19.5429 | 15.6816 | 8.1314 | 9.0009 | 14.866 | 16.1212 | 13.8751 | 12.7493 | [14 empty] | 4.3949 |  | 8.5987 |  |  |  | 21.3252 |  | 14.0508 |  | 4.4806 |  | 11.3695 |  | 1.2673
03/03 01:00:00 | 21.2276 | 21.4121 | 20.9469 | 21.8822 | 22.0231 | 22.0196 | 19.4304 | 15.5608 | 8.0998 | 9.0029 | 14.7831 | 15.9877 | 13.8174 | 16.9851 | [14 empty] | 3.2298 |  | 2.0287 |  |  |  | 78.9484 |  | 63.7165 |  | 4.849 |  | 0.99482 |  | 10.0347
03/03 02:00:00 | 20.9127 | 21.0948 | 20.659 | 21.562 | 21.6094 | 21.6934 | 19.3152 | 14.8763 | 7.931 | 8.742 | 14.1646 | 15.326 | 13.2453 | 19.3245 | [14 empty] | 2.5522 |  | 19.7865 |  |  |  | 129.8123 |  | 111.9904 |  | 26.6249 |  | 15.9878 |  | 36.9572
03/03 03:00:00 | 20.6164 | 20.7968 | 20.3898 | 21.2507 | 21.2305 | 21.4023 | 19.1185 | 13.9916 | 7.6686 | 8.3199 | 13.3405 | 14.4496 | 12.4634 | 20.2719 | [14 empty] | 2.2437 |  | 39.4418 |  |  |  | 158.8431 |  | 142.8505 |  | 48.0439 |  | 33.8986 |  | 60.9714
03/03 04:00:00 | 20.3342 | 20.5124 | 20.1321 | 20.9462 | 20.9339 | 21.1165 | 18.916 | 13.4851 | 7.5277 | 8.1102 | 12.8572 | 13.9314 | 12.037 | 21.4026 | [14 empty] | 2.0113 |  | 62.6871 |  |  |  | 192.5139 |  | 176.6874 |  | 73.0233 |  | 55.8184 |  | 87.7144
03/03 05:00:00 | 20.0519 | 20.23 | 19.8707 | 20.6309 | 20.638 | 20.8206 | 18.756 | 13.1381 | 7.4223 | 7.9995 | 12.5597 | 13.5587 | 11.7459 | 24.1229 | [14 empty] | 1.6793 |  | 120.6654 |  |  |  | 278.9095 |  | 259.962 |  | 133.7061 |  | 111.6013 |  | 153.1899
03/03 06:00:00 | 19.758 | 19.9369 | 19.5954 | 20.3057 | 20.3128 | 20.5013 | 18.6701 | 12.5184 | 7.2712 | 7.7465 | 11.9845 | 12.9404 | 11.2413 | 23.267 | [14 empty] | 1.1836 |  | 115.5315 |  |  |  | 255.8643 |  | 240.8853 |  | 127.2936 |  | 106.6368 |  | 144.6169
03/03 07:00:00 | 19.4689 | 19.6481 | 19.3238 | 19.9781 | 19.9819 | 20.1858 | 18.5705 | 10.1593 | 6.1393 | 6.463 | 11.3672 | 12.2724 | 9.7244 | 23.5196 | [14 empty] | 0.80719 |  | 178.4976 |  |  |  | 302.0746 |  | 290.928 |  | 147.6799 |  | 126.4997 |  | 190.3078
03/03 08:00:00 | 19.241 | 19.4287 | 19.1135 | 19.6599 | 19.6534 | 19.9448 | 19.022 | 12.5917 | 34.4954 | 8.1334 | 39.0003 | 42.7656 | 39.9137 | 86.2904 | [14 empty] | 0.047957 |  | 5431.4879 |  |  |  | 2682.7174 |  | 6108.5121 |  | 2236.3495 |  | 1894.4059 |  | 2150.7923
03/03 09:00:00 | 19.0855 | 19.3847 | 18.9713 | 19.5475 | 19.5488 | 19.9012 | 20.4667 | 37.3533 | 54.9872 | 36.2308 | 59.8158 | 62.4921 | 60.9628 | 62.1781 | [14 empty] | 1.9079 |  | 616.2684 |  |  |  | 51.7086 |  | 673.2615 |  | 5.5801 |  | 0.098583 |  | 1.4768
03/03 10:00:00 | 19.2565 | 20.3543 | 19.1701 | 20.5602 | 20.7569 | 20.9948 | 21.7943 | 48.0334 | 48.7501 | 49.6995 | 54.4238 | 54.929 | 53.5176 | 22.683 | [14 empty] | 6.4406 |  | 642.6423 |  |  |  | 679.4936 |  | 729.89 |  | 1007.4758 |  | 1039.8066 |  | 950.7736
03/03 11:00:00 | 20.4136 | 22.9805 | 20.5232 | 22.8004 | 23.1049 | 23.3819 | 21.9649 | 49.3325 | 36.6683 | 50.1536 | 42.9109 | 42.3283 | 41.5847 | 39.8633 | [14 empty] | 2.4067 |  | 89.6651 |  |  |  | 10.2085 |  | 105.8896 |  | 9.288 |  | 6.0762 |  | 2.9633
03/03 12:00:00 | 21.787 | 24.9531 | 22.6898 | 24.4283 | 24.6476 | 24.9802 | 22.215 | 44.4461 | 32.812 | 40.6753 | 38.6067 | 37.9336 | 37.3792 | 25.2829 | [14 empty] | 0.18316 |  | 367.2285 |  |  |  | 56.6884 |  | 236.9289 |  | 177.524 |  | 160.0418 |  | 146.3219
03/03 13:00:00 | 22.68 | 25.5539 | 24.2096 | 24.9199 | 25.0681 | 25.4301 | 22.239 | 38.8742 | 30.7477 | 36.2227 | 35.9804 | 35.6326 | 34.7231 | 35.5201 | [14 empty] | 0.19452 |  | 11.2505 |  |  |  | 22.7756 |  | 0.49375 |  | 0.21189 |  | 0.012655 |  | 0.63523
03/03 14:00:00 | 23.0912 | 25.6296 | 24.5509 | 24.9336 | 25.0541 | 25.4433 | 22.4515 | 36.7697 | 28.6032 | 34.0858 | 33.8277 | 33.5517 | 32.7488 | 37.1077 | [14 empty] | 0.4093 |  | 0.11424 |  |  |  | 72.3273 |  | 9.1321 |  | 10.7581 |  | 12.645 |  | 18.9997
03/03 15:00:00 | 23.319 | 25.7253 | 24.6541 | 24.9665 | 25.0814 | 25.497 | 22.4561 | 34.2997 | 26.8248 | 31.7222 | 31.4766 | 31.2542 | 30.462 | 23.6223 | [14 empty] | 0.7445 |  | 114.0057 |  |  |  | 10.256 |  | 65.6086 |  | 61.6889 |  | 58.245 |  | 46.7815
03/03 16:00:00 | 23.5669 | 25.9938 | 24.9535 | 25.1934 | 25.3104 | 25.7393 | 22.3147 | 32.6719 | 25.0717 | 29.7612 | 29.8821 | 29.6666 | 28.8437 | 31.6066 | [14 empty] | 1.5681 |  | 1.1347 |  |  |  | 42.7049 |  | 3.4056 |  | 2.974 |  | 3.7637 |  | 7.6339
03/03 17:00:00 | 23.7884 | 26.2202 | 25.2 | 25.376 | 25.5036 | 25.946 | 22.2527 | 30.2578 | 23.4327 | 27.6914 | 27.5497 | 27.3563 | 26.5736 | 36.3008 | [14 empty] | 2.3583 |  | 36.5183 |  |  |  | 165.5872 |  | 74.1209 |  | 76.5814 |  | 80.0041 |  | 94.6176
03/03 18:00:00 | 23.818 | 26.2397 | 25.2265 | 25.333 | 25.4659 | 25.9193 | 22.1914 | 28.5255 | 22.8272 | 26.1379 | 25.6885 | 25.8699 | 25.5695 | 36.9451 | [14 empty] | 2.6456 |  | 70.8898 |  |  |  | 199.3141 |  | 116.7946 |  | 126.7094 |  | 122.6587 |  | 129.4026
03/03 19:00:00 | 23.6961 | 26.1189 | 25.0868 | 25.0979 | 25.2552 | 25.7456 | 21.9866 | 28.5191 | 23.2598 | 25.9206 | 25.8387 | 25.8527 | 25.8184 | 40.0478 | [14 empty] | 2.9224 |  | 132.9116 |  |  |  | 281.8366 |  | 199.5774 |  | 201.8989 |  | 201.5007 |  | 202.4758
03/03 20:00:00 | 23.226 | 25.5733 | 24.5407 | 24.4035 | 24.589 | 25.1247 | 21.8667 | 27.3505 | 22.5475 | 25.0232 | 24.7914 | 24.7864 | 24.6561 | 40.7316 | [14 empty] | 1.8476 |  | 179.0542 |  |  |  | 330.6634 |  | 246.7542 |  | 254.0904 |  | 254.2495 |  | 258.423
03/03 21:00:00 | 22.6699 | 24.9461 | 23.9951 | 23.7279 | 23.8964 | 24.4438 | 21.5694 | 22.0689 | 16.8407 | 19.2373 | 19.5868 | 19.4926 | 19.4648 | 5.1316 | [14 empty] | 1.2111 |  | 286.8733 |  |  |  | 137.1027 |  | 198.9705 |  | 208.952 |  | 206.2386 |  | 205.4408
03/03 22:00:00 | 22.2388 | 24.334 | 23.4954 | 23.1783 | 23.2149 | 23.7897 | 20.7172 | 21.5592 | 16.5877 | 18.8366 | 19.2542 | 19.2646 | 19.163 | 3.7486 | [14 empty] | 2.3152 |  | 317.2186 |  |  |  | 164.8436 |  | 227.6485 |  | 240.4249 |  | 240.7468 |  | 237.6047
03/03 23:00:00 | 21.8479 | 23.738 | 23.0177 | 22.6113 | 22.4747 | 23.1538 | 19.9217 | 20.943 | 16.2572 | 18.316 | 18.7185 | 18.7383 | 18.6572 | 3.2076 | [14 empty] | 3.7104 |  | 314.5438 |  |  |  | 170.2908 |  | 228.2621 |  | 240.5867 |  | 241.2003 |  | 238.6871
03/03 24:00:00 | 21.4292 | 23.1674 | 22.5757 | 21.9864 | 21.8193 | 22.4825 | 19.3799 | 19.6357 | 15.7494 | 17.4324 | 17.697 | 17.7067 | 17.628 | 19.9439 | [14 empty] | 4.1996 |  | 0.094959 |  |  |  | 17.5938 |  | 6.3072 |  | 5.0483 |  | 5.0051 |  | 5.3632
03/04 01:00:00 | 21.04 | 22.6373 | 22.2497 | 21.5213 | 21.2333 | 21.9926 | 19.1326 | 18.5896 | 15.2169 | 16.6311 | 16.7915 | 16.8513 | 16.7614 | 20.9367 | [14 empty] | 3.6379 |  | 5.5092 |  |  |  | 32.7161 |  | 18.5381 |  | 17.1827 |  | 16.6905 |  | 17.4337
03/04 02:00:00 | 20.6941 | 22.2047 | 21.9383 | 21.0707 | 20.7684 | 21.5836 | 18.8625 | 16.9906 | 14.4883 | 15.5011 | 15.3705 | 15.4772 | 15.3266 | 22.8112 | [14 empty] | 3.3546 |  | 33.8801 |  |  |  | 69.2704 |  | 53.4384 |  | 55.3648 |  | 53.7881 |  | 56.0197
03/04 03:00:00 | 20.3586 | 21.8753 | 21.6297 | 20.7208 | 20.384 | 21.2632 | 18.6702 | 16.5445 | 13.9909 | 14.9964 | 14.9837 | 15.0769 | 14.933 | 24.6986 | [14 empty] | 2.8506 |  | 66.4889 |  |  |  | 114.654 |  | 94.1323 |  | 94.378 |  | 92.5765 |  | 95.3664
03/04 04:00:00 | 20.0238 | 21.5152 | 21.3096 | 20.3353 | 19.9895 | 20.8983 | 18.5011 | 16.2655 | 13.6598 | 14.698 | 14.7817 | 14.8684 | 14.728 | 25.6255 | [14 empty] | 2.3186 |  | 87.6107 |  |  |  | 143.1795 |  | 119.4107 |  | 117.589 |  | 115.717 |  | 118.7559
03/04 05:00:00 | 19.7009 | 21.1662 | 20.9971 | 19.9728 | 19.6691 | 20.5479 | 18.381 | 15.2243 | 13.1632 | 13.9386 | 13.8973 | 13.9456 | 13.8341 | 26.0532 | [14 empty] | 1.742 |  | 117.2646 |  |  |  | 166.1517 |  | 146.7634 |  | 147.766 |  | 146.5917 |  | 149.3053
03/04 06:00:00 | 19.3814 | 20.8522 | 20.6847 | 19.6444 | 19.352 | 20.2251 | 18.2982 | 14.6554 | 12.7201 | 13.4356 | 13.3647 | 13.4614 | 13.282 | 26.9916 | [14 empty] | 1.1734 |  | 152.1839 |  |  |  | 203.678 |  | 183.7665 |  | 185.6949 |  | 183.0686 |  | 187.9532
03/04 07:00:00 | 19.0634 | 20.5313 | 20.369 | 19.3069 | 19.0214 | 19.8909 | 18.2495 | 14.1919 | 12.4056 | 13.0233 | 12.9492 | 13.0228 | 12.8938 | 26.6621 | [14 empty] | 0.66245 |  | 155.5072 |  |  |  | 203.2497 |  | 186.0188 |  | 188.044 |  | 186.0315 |  | 189.5674
03/04 08:00:00 | 18.7507 | 20.2069 | 20.056 | 18.9661 | 18.6809 | 19.5524 | 18.3481 | 13.7229 | 12.0467 | 12.6253 | 12.5485 | 12.6234 | 12.4892 | 24.3967 | [14 empty] | 0.16202 |  | 113.929 |  |  |  | 152.5216 |  | 138.5663 |  | 140.3804 |  | 138.6103 |  | 141.7891
03/04 09:00:00 | 18.4423 | 19.8805 | 19.745 | 18.624 | 18.3356 | 19.214 | 19.3571 | 12.603 | 13.2423 | 12.4954 | 12.3442 | 13.0436 | 12.4401 | 71.2607 | [14 empty] | 0.83677 |  | 3440.7237 |  |  |  | 3366.135 |  | 3453.3593 |  | 3471.1491 |  | 3389.2276 |  | 3459.8543
03/04 10:00:00 | 18.248 | 19.6797 | 19.5573 | 18.416 | 18.1304 | 19.019 | 20.6666 | 37.6101 | 35.469 | 38.6957 | 44.5106 | 48.1579 | 46.0976 | 11.5034 | [14 empty] | 5.8497 |  | 681.5616 |  |  |  | 574.3522 |  | 739.4228 |  | 1089.4792 |  | 1343.5558 |  | 1196.7605
03/04 11:00:00 | 18.4973 | 19.7894 | 19.7862 | 18.719 | 18.5087 | 19.4534 | 20.8834 | 46.871 | 41.2244 | 41.8014 | 54.5154 | 56.7929 | 54.675 | 3.8692 | [14 empty] | 5.6933 |  | 1849.1548 |  |  |  | 1395.4083 |  | 1438.8502 |  | 2565.0301 |  | 2800.9169 |  | 2581.2225
03/04 12:00:00 | 19.7522 | 21.2796 | 21.0983 | 20.5462 | 20.4535 | 21.4815 | 20.7664 | 41.4079 | 28.6921 | 31.637 | 45.1399 | 45.6551 | 37.2037 | 3.1675 | [14 empty] | 1.0287 |  | 1462.3285 |  |  |  | 651.5064 |  | 810.5158 |  | 1761.6844 |  | 1805.1989 |  | 1158.4631
03/04 13:00:00 | 20.9425 | 22.7408 | 22.1499 | 22.3795 | 22.3531 | 23.279 | 20.7032 | 36.6637 | 24.2351 | 28.7472 | 37.7768 | 37.3762 | 31.9511 | 30.4051 | [14 empty] | 0.057256 |  | 39.1704 |  |  |  | 38.0688 |  | 2.7486 |  | 54.3427 |  | 48.5966 |  | 2.3902
03/04 14:00:00 | 21.5992 | 23.28 | 22.5501 | 23.2353 | 23.2317 | 23.8265 | 20.9851 | 34.4449 | 23.185 | 27.4198 | 34.7846 | 34.4688 | 30.8112 | 3.7501 | [14 empty] | 0.37707 |  | 942.1753 |  |  |  | 377.7161 |  | 560.2547 |  | 963.145 |  | 943.6399 |  | 732.3063
03/04 15:00:00 | 21.8742 | 23.5302 | 22.8265 | 23.5373 | 23.5667 | 24.0456 | 20.95 | 32.9254 | 21.9016 | 25.9896 | 33.1965 | 32.9868 | 29.346 | 3.2223 | [14 empty] | 0.85413 |  | 882.2726 |  |  |  | 348.9155 |  | 518.3491 |  | 898.4537 |  | 885.927 |  | 682.446
03/04 16:00:00 | 22.0412 | 23.7392 | 23.0476 | 23.7077 | 23.7737 | 24.2458 | 20.801 | 29.1304 | 20.0371 | 23.283 | 29.2207 | 29.1069 | 25.6953 | 22.8299 | [14 empty] | 1.5381 |  | 39.6964 |  |  |  | 7.8 |  | 0.20529 |  | 40.8425 |  | 39.4011 |  | 8.2103
03/04 17:00:00 | 22.2383 | 23.9915 | 23.3023 | 23.9215 | 24.0208 | 24.503 | 20.973 | 27.3597 | 18.4381 | 21.6259 | 27.1673 | 26.8062 | 23.4677 | 10.1726 | [14 empty] | 1.601 |  | 295.3959 |  |  |  | 68.3191 |  | 131.1769 |  | 288.8195 |  | 276.6772 |  | 176.76
03/04 18:00:00 | 22.4774 | 24.2967 | 23.5916 | 24.1631 | 24.294 | 24.7839 | 20.9654 | 25.7684 | 17.3627 | 20.3708 | 25.3325 | 24.9363 | 21.9031 | 35.8797 | [14 empty] | 2.2862 |  | 102.2384 |  |  |  | 342.8795 |  | 240.5263 |  | 111.2439 |  | 119.758 |  | 195.3456
03/04 19:00:00 | 22.6972 | 24.6175 | 23.8523 | 24.3434 | 24.5259 | 25.0068 | 20.9474 | 26.9143 | 17.8294 | 21.197 | 26.2965 | 26.1843 | 23.7255 | 31.0352 | [14 empty] | 3.0618 |  | 16.9817 |  |  |  | 174.3916 |  | 96.7897 |  | 22.4551 |  | 23.5311 |  | 53.4313
03/04 20:00:00 | 22.5893 | 24.5155 | 23.7357 | 24.1395 | 24.3221 | 24.7749 | 20.6409 | 22.3923 | 14.1358 | 16.9588 | 21.1081 | 20.9242 | 19.2593 | 4.6088 | [14 empty] | 3.7961 |  | 316.2535 |  |  |  | 90.7631 |  | 152.5228 |  | 272.2262 |  | 266.1928 |  | 214.6365
03/04 21:00:00 | 22.2557 | 24.0569 | 23.3907 | 23.6957 | 23.7939 | 24.2523 | 19.8573 | 21.8982 | 14.1261 | 16.7385 | 20.7469 | 20.6134 | 19.0331 | 12.2029 | [14 empty] | 5.7524 |  | 94.0005 |  |  |  | 3.6987 |  | 20.5719 |  | 73.0008 |  | 70.7369 |  | 46.6521
03/04 22:00:00 | 21.9321 | 23.6285 | 23.065 | 23.1856 | 23.1906 | 23.7324 | 19.2879 | 21.14 | 13.897 | 16.3048 | 20.1644 | 20.0455 | 18.5319 | 19.9535 | [14 empty] | 6.9916 |  | 1.4076 |  |  |  | 36.6817 |  | 13.3133 |  | 0.044463 |  | 0.0084574 |  | 2.0211
03/04 23:00:00 | 21.5958 | 23.1799 | 22.7248 | 22.7338 | 22.6628 | 23.1786 | 19.0484 | 20.4651 | 13.6327 | 15.8831 | 19.5607 | 19.4791 | 18.0385 | 21.2876 | [14 empty] | 6.4892 |  | 0.6765 |  |  |  | 58.5982 |  | 29.2084 |  | 2.9823 |  | 3.2708 |  | 10.5569
03/04 24:00:00 | 21.2452 | 22.7235 | 22.3687 | 22.2553 | 22.1062 | 22.6389 | 18.8437 | 19.9258 | 13.4016 | 15.5527 | 19.1614 | 19.0977 | 17.7512 | 23.3462 | [14 empty] | 5.7674 |  | 11.6987 |  |  |  | 98.8944 |  | 60.7382 |  | 17.5121 |  | 18.0493 |  | 31.3038
03/05 01:00:00 | 20.9506 | 22.3281 | 21.9979 | 21.8393 | 21.6285 | 22.2179 | 18.6593 | 19.2552 | 13.1291 | 15.1127 | 18.4604 | 18.4557 | 17.1233 | 23.6957 | [14 empty] | 5.2503 |  | 19.7177 |  |  |  | 111.6511 |  | 73.6663 |  | 27.4079 |  | 27.4569 |  | 43.1957
03/05 02:00:00 | 20.6055 | 21.9172 | 21.6012 | 21.3589 | 21.1108 | 21.763 | 18.4893 | 18.7713 | 12.9034 | 14.7941 | 18.1519 | 18.1328 | 16.8748 | 26.0501 | [14 empty] | 4.4782 |  | 52.9807 |  |  |  | 172.8364 |  | 126.697 |  | 62.3818 |  | 62.6841 |  | 84.1854
03/05 03:00:00 | 20.2486 | 21.4805 | 21.2647 | 20.8701 | 20.6562 | 21.2963 | 18.3985 | 18.2449 | 12.6301 | 14.4668 | 17.6912 | 17.67 | 16.4694 | 26.1749 | [14 empty] | 3.4228 |  | 62.8849 |  |  |  | 183.4608 |  | 137.0793 |  | 71.9727 |  | 72.3321 |  | 94.196
03/05 04:00:00 | 19.9055 | 21.0295 | 20.9339 | 20.3916 | 20.1885 | 20.8331 | 18.3071 | 17.4563 | 12.3755 | 13.9395 | 16.9659 | 16.947 | 15.8135 | 27.9579 | [14 empty] | 2.5549 |  | 110.2831 |  |  |  | 242.8096 |  | 196.5139 |  | 120.8243 |  | 121.2384 |  | 147.4869
03/05 05:00:00 | 19.5563 | 20.6669 | 20.592 | 19.9255 | 19.7195 | 20.3763 | 18.2162 | 16.7072 | 12.019 | 13.4819 | 16.2642 | 16.2678 | 15.1899 | 28.9588 | [14 empty] | 1.7959 |  | 150.1022 |  |  |  | 286.9557 |  | 239.5343 |  | 161.1521 |  | 161.0619 |  | 189.5816
03/05 06:00:00 | 19.1953 | 20.2709 | 20.2366 | 19.4642 | 19.2466 | 19.9201 | 18.1301 | 16.3584 | 11.7816 | 13.2129 | 15.9267 | 15.9556 | 14.907 | 29.2106 | [14 empty] | 1.1346 |  | 165.1776 |  |  |  | 303.7686 |  | 255.9254 |  | 176.4606 |  | 175.693 |  | 204.5913
03/05 07:00:00 | 18.8366 | 19.8851 | 19.8808 | 19.0964 | 18.7803 | 19.5536 | 18.0625 | 15.7248 | 11.5333 | 12.8242 | 15.3517 | 15.3892 | 14.3831 | 29.5472 | [14 empty] | 0.59921 |  | 191.0572 |  |  |  | 324.5 |  | 279.6569 |  | 201.5126 |  | 200.447 |  | 229.9484
03/05 08:00:00 | 18.4756 | 19.5368 | 19.5231 | 18.7399 | 18.3201 | 19.1469 | 18.2268 | 15.157 | 11.2461 | 12.4342 | 14.8068 | 34.6873 | 13.8866 | 25.2691 | [14 empty] | 0.061872 |  | 102.2532 |  |  |  | 196.6444 |  | 164.7336 |  | 109.4596 |  | 88.7032 |  | 129.561
03/05 09:00:00 | 18.1269 | 19.1909 | 19.1766 | 18.3809 | 18.1122 | 18.7599 | 19.2603 | 13.4726 | 11.8623 | 11.8448 | 14.0317 | 63.5437 | 13.1299 | 79.8639 | [14 empty] | 1.2847 |  | 4407.8096 |  |  |  | 4624.2138 |  | 4626.6008 |  | 4333.8735 |  | 266.3507 |  | 4453.4224
03/05 10:00:00 | 17.933 | 19.0052 | 18.9988 | 18.1858 | 19.2586 | 18.5819 | 20.6631 | 39.134 | 43.8357 | 39.3975 | 46.6961 | 57.0227 | 47.7925 | 5.6713 | [14 empty] | 7.4532 |  | 1119.7533 |  |  |  | 1456.5249 |  | 1137.4584 |  | 1683.0365 |  | 2636.9673 |  | 1774.1993
03/05 11:00:00 | 18.236 | 19.4308 | 19.3471 | 18.5793 | 21.3167 | 19.1356 | 20.8808 | 47.9633 | 50.5145 | 48.8315 | 55.5255 | 43.5855 | 55.8937 | 3.6823 | [14 empty] | 6.9954 |  | 1960.813 |  |  |  | 2193.2575 |  | 2038.4499 |  | 2687.7237 |  | 1592.2672 |  | 2726.036
03/05 12:00:00 | 19.6309 | 21.5482 | 20.906 | 20.5722 | 22.9537 | 21.3391 | 20.8833 | 41.2886 | 34.2294 | 36.5089 | 39.5189 | 38.1141 | 38.4742 | 3.101 | [14 empty] | 1.5685 |  | 1458.2964 |  |  |  | 968.9772 |  | 1116.0882 |  | 1326.2653 |  | 1225.916 |  | 1251.2663
03/05 13:00:00 | 21.0018 | 23.6912 | 22.6013 | 22.5004 | 23.6936 | 23.3242 | 20.9198 | 35.3663 | 28.3649 | 31.1277 | 32.9186 | 35.2906 | 31.6182 | 3.0127 | [14 empty] | 0.0067358 |  | 1046.7553 |  |  |  | 642.7336 |  | 790.4548 |  | 894.3612 |  | 1041.8645 |  | 818.273
03/05 14:00:00 | 21.7403 | 24.5844 | 23.3648 | 23.2205 | 24.1172 | 24.0893 | 20.9972 | 33.9165 | 26.9688 | 29.8036 | 31.9897 | 33.8262 | 30.9776 | 2.8641 | [14 empty] | 0.55219 |  | 964.2557 |  |  |  | 581.0376 |  | 725.7395 |  | 848.3043 |  | 958.6539 |  | 790.3728
03/05 15:00:00 | 22.1468 | 24.9848 | 23.7727 | 23.5235 | 24.4936 | 24.4363 | 21.1232 | 30.8147 | 24.7028 | 27.2729 | 29.0152 | 30.4462 | 28.121 | 2.7575 | [14 empty] | 1.0478 |  | 787.2085 |  |  |  | 481.5959 |  | 601.0064 |  | 689.4676 |  | 766.667 |  | 643.3095
03/05 16:00:00 | 22.5079 | 25.3589 | 24.1651 | 23.8487 | 24.8703 | 24.8098 | 21.2841 | 27.8726 | 21.8829 | 24.8447 | 26.0191 | 26.6962 | 24.9165 | 2.7629 | [14 empty] | 1.4977 |  | 630.499 |  |  |  | 365.5747 |  | 487.605 |  | 540.851 |  | 572.8007 |  | 490.7829
03/05 17:00:00 | 22.7906 | 25.6913 | 24.4977 | 24.1323 | 25.1752 | 25.1485 | 21.3819 | 26.2134 | 19.7512 | 23.2597 | 24.2819 | 24.5661 | 22.7552 | 2.6923 | [14 empty] | 1.9846 |  | 553.2454 |  |  |  | 291.0082 |  | 423.02 |  | 466.1108 |  | 478.4661 |  | 402.5203
03/05 18:00:00 | 23.0793 | 26.0072 | 24.8224 | 24.4252 | 25.448 | 25.4721 | 21.3214 | 23.9358 | 18.2394 | 21.174 | 22.0379 | 22.3571 | 20.3585 | 2.771 | [14 empty] | 3.0905 |  | 447.9475 |  |  |  | 239.2721 |  | 338.671 |  | 371.2153 |  | 383.6179 |  | 309.3192
03/05 19:00:00 | 23.3491 | 26.2968 | 25.1157 | 24.6799 | 25.6559 | 25.7486 | 20.981 | 24.6754 | 20.0217 | 21.6425 | 22.7186 | 24.2529 | 22.2313 | 18.9327 | [14 empty] | 5.6077 |  | 32.9779 |  |  |  | 1.1858 |  | 7.3427 |  | 14.3329 |  | 28.3047 |  | 10.8804
03/05 20:00:00 | 23.3649 | 26.2495 | 25.1635 | 24.6491 | 25.5384 | 25.6476 | 20.8976 | 20.7283 | 15.4706 | 17.0995 | 18.3995 | 19.3225 | 18.1107 | 3.8776 | [14 empty] | 6.0876 |  | 283.9458 |  |  |  | 134.3987 |  | 174.8194 |  | 210.8852 |  | 238.5459 |  | 202.5807
03/05 21:00:00 | 23.1851 | 25.9752 | 24.9719 | 24.3592 | 25.1866 | 25.326 | 20.5464 | 19.7598 | 15.163 | 16.5881 | 17.6878 | 18.5865 | 17.4364 | 3.2341 | [14 empty] | 6.9627 |  | 273.0998 |  |  |  | 142.3001 |  | 178.3309 |  | 208.9105 |  | 235.6977 |  | 201.707
03/05 22:00:00 | 22.9628 | 25.6795 | 24.7498 | 24.0348 | 24.7763 | 24.9835 | 20.0963 | 18.0402 | 14.552 | 15.5001 | 16.1921 | 17.0475 | 15.9443 | 2.8514 | [14 empty] | 8.2164 |  | 230.6982 |  |  |  | 136.9037 |  | 159.9897 |  | 177.9746 |  | 201.5288 |  | 171.4244
03/05 23:00:00 | 22.7069 | 25.341 | 24.4902 | 23.6645 | 24.3095 | 24.5964 | 19.7022 | 17.3999 | 14.0746 | 14.9275 | 15.7182 | 16.5352 | 15.4826 | 18.5872 | [14 empty] | 9.0282 |  | 1.4096 |  |  |  | 20.3635 |  | 13.3935 |  | 8.2311 |  | 4.2105 |  | 9.6385
03/05 24:00:00 | 22.4984 | 25.0404 | 24.2718 | 23.3544 | 23.9199 | 24.2688 | 19.6557 | 17.1202 | 13.7349 | 14.6321 | 15.533 | 16.3732 | 15.3193 | 14.4956 | [14 empty] | 8.0807 |  | 6.8881 |  |  |  | 0.57872 |  | 0.018612 |  | 1.0761 |  | 3.5251 |  | 0.67847
03/06 01:00:00 | 22.3043 | 24.749 | 24.0693 | 23.0575 | 23.5953 | 23.9519 | 19.6828 | 16.5177 | 13.3165 | 14.1763 | 15.0237 | 15.8352 | 14.8288 | 13.2079 | [14 empty] | 6.8724 |  | 10.9551 |  |  |  | 0.011805 |  | 0.93774 |  | 3.2973 |  | 6.9028 |  | 2.6273
03/06 02:00:00 | 22.141 | 24.4899 | 23.898 | 22.852 | 23.3137 | 23.6781 | 19.68 | 15.9512 | 12.9305 | 13.7199 | 14.5416 | 15.3289 | 14.3626 | 14.1192 | [14 empty] | 6.0564 |  | 3.3564 |  |  |  | 1.4129 |  | 0.1594 |  | 0.17842 |  | 1.4634 |  | 0.059281
03/06 03:00:00 | 21.9604 | 24.2763 | 23.7061 | 22.6409 | 23.0197 | 23.4495 | 19.6582 | 14.7402 | 12.4683 | 12.8833 | 13.4397 | 14.2286 | 13.3184 | 15.027 | [14 empty] | 5.3001 |  | 0.082246 |  |  |  | 6.5468 |  | 4.5956 |  | 2.5196 |  | 0.63749 |  | 2.9192
03/06 04:00:00 | 21.7669 | 24.0707 | 23.5027 | 22.4145 | 22.768 | 23.2196 | 19.646 | 13.6194 | 11.7909 | 12.0787 | 12.443 | 13.1487 | 12.2733 | 15.697 | [14 empty] | 4.4984 |  | 4.3165 |  |  |  | 15.2578 |  | 13.0926 |  | 10.5888 |  | 6.4941 |  | 11.722
03/06 05:00:00 | 21.5704 | 23.8483 | 23.2968 | 22.182 | 22.5242 | 22.9795 | 19.6627 | 13.0417 | 11.318 | 11.5405 | 11.9013 | 12.5918 | 11.7577 | 14.1923 | [14 empty] | 3.6392 |  | 1.324 |  |  |  | 8.2618 |  | 7.0325 |  | 5.2491 |  | 2.5618 |  | 5.9273
03/06 06:00:00 | 21.3724 | 23.6181 | 23.0784 | 21.943 | 22.2706 | 22.7341 | 19.6893 | 11.2438 | 11.1698 | 9.7622 | 12.2812 | 12.948 | 12.1738 | 8.6344 | [14 empty] | 2.833 |  | 6.8089 |  |  |  | 6.428 |  | 1.2718 |  | 13.2992 |  | 18.6069 |  | 12.5272
03/06 07:00:00 | 21.2023 | 23.3835 | 22.8981 | 21.6989 | 22.0024 | 22.4891 | 19.6714 | 10.0313 | 10.735 | 9.2111 | 11.0869 | 11.726 | 10.9591 | 14.1826 | [14 empty] | 2.3436 |  | 17.2334 |  |  |  | 11.8858 |  | 24.7156 |  | 9.583 |  | 6.0349 |  | 10.3907
03/06 08:00:00 | 21.0865 | 23.1724 | 22.7788 | 21.4785 | 21.7567 | 22.2559 | 20.2686 | 12.3333 | 12.1808 | 11.7458 | 11.8825 | 13.1153 | 11.8601 | 77.8635 | [14 empty] | 0.66906 |  | 4294.2135 |  |  |  | 4314.2157 |  | 4371.55 |  | 4353.4962 |  | 4192.3332 |  | 4356.4484
03/06 09:00:00 | 20.9952 | 23.0342 | 22.6858 | 21.3367 | 21.6087 | 22.1081 | 21.7332 | 34.9404 | 13.2006 | 13.0866 | 13.517 | 14.1735 | 12.7116 | 39.9723 | [14 empty] | 0.54462 |  | 25.3199 |  |  |  | 716.7223 |  | 722.8404 |  | 699.8816 |  | 665.5781 |  | 743.148
03/06 10:00:00 | 21.2881 | 23.064 | 22.7396 | 21.3713 | 21.6139 | 22.1315 | 22.3131 | 33.9643 | 11.8612 | 11.4985 | 20.2484 | 17.4545 | 11.694 | 9.6063 | [14 empty] | 1.0508 |  | 593.3127 |  |  |  | 5.0845 |  | 3.5805 |  | 113.2548 |  | 61.5952 |  | 4.3585
03/06 11:00:00 | 22.2855 | 23.2529 | 22.989 | 21.72 | 21.8634 | 22.3516 | 22.4109 | 28.5015 | 11.0396 | 10.9348 | 29.9161 | 25.0343 | 11.449 | 16.3578 | [14 empty] | 0.015713 |  | 147.4694 |  |  |  | 28.2837 |  | 29.409 |  | 183.8268 |  | 75.2806 |  | 24.0963
03/06 12:00:00 | 23.0728 | 23.5147 | 23.2643 | 22.3543 | 22.3442 | 22.6307 | 22.6944 | 26.0315 | 10.1511 | 10.0615 | 23.4259 | 19.6184 | 10.0349 | 4.2511 | [14 empty] | 0.14316 |  | 474.3855 |  |  |  | 34.8107 |  | 33.7608 |  | 367.6725 |  | 236.1539 |  | 33.4527
03/06 13:00:00 | 23.5623 | 23.8201 | 23.5468 | 23.2228 | 23.1007 | 22.935 | 22.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 3.166 | [14 empty] | 0.66402 |  | 10.0236 |  |  |  | 10.0236 |  | 10.0236 |  | 10.0236 |  | 10.0236 |  | 10.0236
03/06 14:00:00 | 23.266 | 23.8268 | 23.4967 | 23.3262 | 23.2095 | 22.9252 | 22.6987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.3218 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/06 15:00:00 | 23.0023 | 23.8658 | 23.5337 | 23.2299 | 23.1568 | 22.9707 | 22.5273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.2256 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/06 16:00:00 | 23.0788 | 24.1505 | 23.8353 | 23.3946 | 23.349 | 23.2665 | 22.2897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.62271 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/06 17:00:00 | 23.1413 | 24.3193 | 24.0107 | 23.4899 | 23.4527 | 23.431 | 22.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 18.4515 | [14 empty] | 1.2808 |  | 340.4597 |  |  |  | 340.4597 |  | 340.4597 |  | 340.4597 |  | 340.4597 |  | 340.4597
03/06 18:00:00 | 23.0189 | 24.2624 | 23.9403 | 23.3795 | 23.3394 | 23.3537 | 22.0921 | 0 | 0 | 0 | 0 | 0 | 0 | 18.5017 | [14 empty] | 0.85909 |  | 342.3122 |  |  |  | 342.3122 |  | 342.3122 |  | 342.3122 |  | 342.3122 |  | 342.3122
03/06 19:00:00 | 22.79 | 24.111 | 23.7724 | 23.165 | 23.1163 | 23.1748 | 22.1625 | 0 | 0 | 0 | 0 | 0 | 0 | 18.5534 | [14 empty] | 0.39386 |  | 344.2305 |  |  |  | 344.2305 |  | 344.2305 |  | 344.2305 |  | 344.2305 |  | 344.2305
03/06 20:00:00 | 22.3137 | 23.7042 | 23.3425 | 22.702 | 22.6361 | 22.7328 | 22.1921 | 0 | 0 | 0 | 0 | 0 | 0 | 18.1709 | [14 empty] | 0.01479 |  | 330.1819 |  |  |  | 330.1819 |  | 330.1819 |  | 330.1819 |  | 330.1819 |  | 330.1819
03/06 21:00:00 | 21.8453 | 23.2687 | 22.9119 | 22.245 | 22.158 | 22.2825 | 22.1157 | 0 | 0 | 0 | 0 | 0 | 0 | 3.898 | [14 empty] | 0.073138 |  | 15.1941 |  |  |  | 15.1941 |  | 15.1941 |  | 15.1941 |  | 15.1941 |  | 15.1941
03/06 22:00:00 | 21.4915 | 22.9218 | 22.5838 | 21.8965 | 21.7895 | 21.9325 | 21.801 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1019 | [14 empty] | 0.095819 |  | 9.6216 |  |  |  | 9.6216 |  | 9.6216 |  | 9.6216 |  | 9.6216 |  | 9.6216
03/06 23:00:00 | 21.2558 | 22.6785 | 22.3633 | 21.6615 | 21.5387 | 21.6941 | 21.4655 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8626 | [14 empty] | 0.043982 |  | 8.1944 |  |  |  | 8.1944 |  | 8.1944 |  | 8.1944 |  | 8.1944 |  | 8.1944
03/06 24:00:00 | 21.051 | 22.4571 | 22.1714 | 21.455 | 21.3168 | 21.4843 | 21.1841 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0024 | [14 empty] | 0.017702 |  | 9.0142 |  |  |  | 9.0142 |  | 9.0142 |  | 9.0142 |  | 9.0142 |  | 9.0142
03/07 01:00:00 | 20.8502 | 22.2369 | 21.9835 | 21.2517 | 21.0971 | 21.2774 | 20.943 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9111 | [14 empty] | 0.0086133 |  | 8.4747 |  |  |  | 8.4747 |  | 8.4747 |  | 8.4747 |  | 8.4747 |  | 8.4747
03/07 02:00:00 | 20.7429 | 22.114 | 21.8852 | 21.1412 | 20.9744 | 21.1644 | 20.7218 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8606 | [14 empty] | 0.00044454 |  | 8.1833 |  |  |  | 8.1833 |  | 8.1833 |  | 8.1833 |  | 8.1833 |  | 8.1833
03/07 03:00:00 | 20.6339 | 21.9888 | 21.7838 | 21.028 | 20.849 | 21.0495 | 20.5554 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8476 | [14 empty] | 0.0061617 |  | 8.1088 |  |  |  | 8.1088 |  | 8.1088 |  | 8.1088 |  | 8.1088 |  | 8.1088
03/07 04:00:00 | 20.5326 | 21.8705 | 21.6895 | 20.9219 | 20.7306 | 20.9415 | 20.4411 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8024 | [14 empty] | 0.0083751 |  | 7.8535 |  |  |  | 7.8535 |  | 7.8535 |  | 7.8535 |  | 7.8535 |  | 7.8535
03/07 05:00:00 | 20.4362 | 21.7568 | 21.5997 | 20.8205 | 20.617 | 20.8383 | 20.3476 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8226 | [14 empty] | 0.0078476 |  | 7.967 |  |  |  | 7.967 |  | 7.967 |  | 7.967 |  | 7.967 |  | 7.967
03/07 06:00:00 | 20.346 | 21.6487 | 21.5158 | 20.7248 | 20.5093 | 20.7406 | 20.2309 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7974 | [14 empty] | 0.013237 |  | 7.8255 |  |  |  | 7.8255 |  | 7.8255 |  | 7.8255 |  | 7.8255 |  | 7.8255
03/07 07:00:00 | 20.2625 | 21.5468 | 21.4385 | 20.6357 | 20.4086 | 20.6499 | 20.1461 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7557 | [14 empty] | 0.013555 |  | 7.5937 |  |  |  | 7.5937 |  | 7.5937 |  | 7.5937 |  | 7.5937 |  | 7.5937
03/07 08:00:00 | 20.1864 | 21.4516 | 21.3681 | 20.5539 | 20.3155 | 20.5665 | 20.6814 | 0 | 0 | 0 | 0 | 0 | 0 | 67.9059 | [14 empty] | 0.2451 |  | 4611.2118 |  |  |  | 4611.2118 |  | 4611.2118 |  | 4611.2118 |  | 4611.2118 |  | 4611.2118
03/07 09:00:00 | 20.1416 | 21.3852 | 21.3302 | 20.502 | 20.2532 | 20.5159 | 22.1296 | 0 | 0 | 0 | 0 | 0 | 0 | 18.6707 | [14 empty] | 3.9522 |  | 348.5969 |  |  |  | 348.5969 |  | 348.5969 |  | 348.5969 |  | 348.5969 |  | 348.5969
03/07 10:00:00 | 20.2398 | 21.4264 | 21.4445 | 20.5918 | 20.3273 | 20.6056 | 22.8359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 6.7395 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/07 11:00:00 | 20.6445 | 21.8633 | 21.8805 | 20.9874 | 20.7682 | 21.1364 | 22.8495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.862 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/07 12:00:00 | 21.2439 | 22.5032 | 22.5106 | 21.5827 | 21.4236 | 21.8125 | 22.7758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.3469 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/07 13:00:00 | 21.6686 | 22.9105 | 22.9507 | 22.0041 | 21.8137 | 22.2139 | 22.7858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.2481 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/07 14:00:00 | 21.6913 | 22.9482 | 22.9756 | 22.0268 | 21.8203 | 22.2291 | 22.4823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.62571 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/07 15:00:00 | 21.7147 | 22.9742 | 23.0036 | 22.0498 | 21.8295 | 22.2478 | 22.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.23669 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/07 16:00:00 | 21.9372 | 23.1942 | 23.2362 | 22.2658 | 22.0329 | 22.4597 | 22.187 | 0 | 0 | 0 | 0 | 0 | 0 | 17.8304 | [14 empty] | 0.062368 |  | 317.9247 |  |  |  | 317.9247 |  | 317.9247 |  | 317.9247 |  | 317.9247 |  | 317.9247
03/07 17:00:00 | 22.0815 | 23.3753 | 23.3854 | 22.403 | 22.1609 | 22.6009 | 22.5471 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3419 | [14 empty] | 0.2168 |  | 18.8518 |  |  |  | 18.8518 |  | 18.8518 |  | 18.8518 |  | 18.8518 |  | 18.8518
03/07 18:00:00 | 22.0517 | 23.3902 | 23.352 | 22.3678 | 22.1185 | 22.5825 | 22.5065 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1169 | [14 empty] | 0.20685 |  | 9.7148 |  |  |  | 9.7148 |  | 9.7148 |  | 9.7148 |  | 9.7148 |  | 9.7148
03/07 19:00:00 | 21.9768 | 23.3356 | 23.2716 | 22.2863 | 22.0263 | 22.4879 | 22.2824 | 0 | 0 | 0 | 0 | 0 | 0 | 20.037 | [14 empty] | 0.093438 |  | 401.4824 |  |  |  | 401.4824 |  | 401.4824 |  | 401.4824 |  | 401.4824 |  | 401.4824
03/07 20:00:00 | 21.7433 | 23.1366 | 23.0282 | 22.0466 | 21.7763 | 22.2369 | 22.3691 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6631 | [14 empty] | 0.39163 |  | 75.05 |  |  |  | 75.05 |  | 75.05 |  | 75.05 |  | 75.05 |  | 75.05
03/07 21:00:00 | 21.4809 | 22.8682 | 22.7563 | 21.7792 | 21.4946 | 21.9531 | 22.3161 | 0 | 0 | 0 | 0 | 0 | 0 | 3.811 | [14 empty] | 0.69756 |  | 14.5238 |  |  |  | 14.5238 |  | 14.5238 |  | 14.5238 |  | 14.5238 |  | 14.5238
03/07 22:00:00 | 21.3065 | 22.6761 | 22.575 | 21.5997 | 21.304 | 21.7598 | 22.1433 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1008 | [14 empty] | 0.70028 |  | 9.6148 |  |  |  | 9.6148 |  | 9.6148 |  | 9.6148 |  | 9.6148 |  | 9.6148
03/07 23:00:00 | 21.1936 | 22.499 | 22.4572 | 21.4822 | 21.1357 | 21.5879 | 21.7279 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0872 | [14 empty] | 0.2854 |  | 9.5308 |  |  |  | 9.5308 |  | 9.5308 |  | 9.5308 |  | 9.5308 |  | 9.5308
03/07 24:00:00 | 21.011 | 22.2395 | 22.2653 | 21.2896 | 20.8832 | 21.3326 | 21.1844 | 27.2618 | 13.7728 | 12.0399 | 25.3405 | 23.2833 | 14.0549 | 3.0097 | [14 empty] | 0.030071 |  | 588.163 |  |  |  | 115.8429 |  | 81.543 |  | 498.6618 |  | 411.0179 |  | 121.9949
03/08 01:00:00 | 21.0726 | 21.9976 | 22.0169 | 21.2454 | 20.7768 | 21.0857 | 20.6597 | 21.7947 | 8.4388 | 8.7118 | 17.294 | 14.9411 | 9.4997 | 2.81 | [14 empty] | 0.17049 |  | 360.416 |  |  |  | 31.6835 |  | 34.8311 |  | 209.7864 |  | 147.1622 |  | 44.7517
03/08 02:00:00 | 21.1782 | 21.779 | 21.7625 | 21.216 | 20.6691 | 20.8595 | 20.2749 | 20.3965 | 7.8171 | 8.2259 | 16.0744 | 13.8231 | 8.853 | 2.8877 | [14 empty] | 0.81607 |  | 306.5568 |  |  |  | 24.2988 |  | 28.4963 |  | 173.8879 |  | 119.5823 |  | 35.5848
03/08 03:00:00 | 21.2396 | 21.5937 | 21.5859 | 21.1697 | 20.5753 | 20.6679 | 19.9632 | 16.3092 | 6.6707 | 6.8537 | 13.6716 | 12.0554 | 7.8589 | 2.8949 | [14 empty] | 1.6292 |  | 179.9426 |  |  |  | 14.2564 |  | 15.6719 |  | 116.1358 |  | 83.9146 |  | 24.6404
03/08 04:00:00 | 21.2351 | 21.4556 | 21.4594 | 21.1096 | 20.4877 | 20.5299 | 19.6913 | 16.1006 | 6.6717 | 8.0958 | 15.3931 | 13.2479 | 7.8852 | 2.9257 | [14 empty] | 2.3832 |  | 173.5766 |  |  |  | 14.0327 |  | 26.7293 |  | 155.4349 |  | 106.5482 |  | 24.5969
03/08 05:00:00 | 21.2077 | 21.3549 | 21.3468 | 21.0427 | 20.382 | 20.4275 | 19.5049 | 15.5438 | 6.5315 | 6.6087 | 12.9063 | 11.3806 | 7.6394 | 12.7244 | [14 empty] | 2.8998 |  | 7.9491 |  |  |  | 38.3526 |  | 37.4018 |  | 0.033077 |  | 1.8059 |  | 25.8574
03/08 06:00:00 | 21.1708 | 21.2529 | 21.2206 | 20.9567 | 20.2722 | 20.324 | 19.5334 | 14.9521 | 6.3827 | 6.4874 | 12.5507 | 11.0677 | 7.3862 | 11.6621 | [14 empty] | 2.681 |  | 10.824 |  |  |  | 27.8729 |  | 26.7776 |  | 0.78962 |  | 0.35334 |  | 18.2839
03/08 07:00:00 | 21.1235 | 21.1479 | 21.1247 | 20.8821 | 20.1858 | 20.2154 | 19.5066 | 14.6295 | 6.2469 | 6.4403 | 12.3178 | 10.8863 | 7.2498 | 15.5451 | [14 empty] | 2.6143 |  | 0.83833 |  |  |  | 86.4558 |  | 82.8966 |  | 10.415 |  | 21.7035 |  | 68.8117
03/08 08:00:00 | 21.0632 | 21.0371 | 21.0236 | 20.7958 | 20.0903 | 20.0964 | 20.1128 | 17.3543 | 33.259 | 30.9381 | 40.1351 | 13.747 | 37.9255 | 75.1646 | [14 empty] | 0.90338 |  | 3342.0262 |  |  |  | 1756.0735 |  | 1955.9826 |  | 1227.0642 |  | 3772.1166 |  | 1386.7508
03/08 09:00:00 | 21.0054 | 21.0491 | 21.0659 | 20.8654 | 20.0113 | 20.1375 | 21.9477 | 36.4519 | 52.0301 | 48.5595 | 55.962 | 46.3386 | 57.9966 | 25.6714 | [14 empty] | 0.88789 |  | 116.2182 |  |  |  | 694.7793 |  | 523.8633 |  | 917.5196 |  | 427.1345 |  | 1044.9175
03/08 10:00:00 | 21.403 | 22.5251 | 22.1762 | 22.4098 | 20.5279 | 21.8709 | 22.7395 | 33.5798 | 26.6932 | 31.7042 | 35.6277 | 54.099 | 36.0252 | 4.0834 | [14 empty] | 1.7864 |  | 870.041 |  |  |  | 511.2017 |  | 762.9085 |  | 995.0425 |  | 2501.5618 |  | 1020.2809
03/08 11:00:00 | 22.9692 | 25.4528 | 24.9337 | 24.9778 | 23.3255 | 24.752 | 22.9671 | 27.4795 | 19.2052 | 27.8282 | 30.2503 | 34.2713 | 29.0661 | 3.3388 | [14 empty] | 4.2848e-06 |  | 582.7761 |  |  |  | 251.7433 |  | 599.7306 |  | 724.2272 |  | 956.8219 |  | 661.8943
03/08 12:00:00 | 24.489 | 26.9648 | 26.3241 | 26.209 | 25.7458 | 26.143 | 23.1013 | 24.5962 | 14.4702 | 23.3081 | 26.3641 | 26.8399 | 24.6346 | 3.0909 | [14 empty] | 1.9257 |  | 462.4786 |  |  |  | 129.4871 |  | 408.7359 |  | 541.6394 |  | 564.0143 |  | 464.1277
03/08 13:00:00 | 25.2149 | 27.5834 | 26.9097 | 26.7287 | 26.5602 | 26.815 | 23.1561 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9187 | [14 empty] | 4.2385 |  | 8.5187 |  |  |  | 8.5187 |  | 8.5187 |  | 8.5187 |  | 8.5187 |  | 8.5187
03/08 14:00:00 | 24.8155 | 27.341 | 26.5479 | 26.3308 | 26.1626 | 26.5213 | 23.2027 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7741 | [14 empty] | 2.6013 |  | 7.6955 |  |  |  | 7.6955 |  | 7.6955 |  | 7.6955 |  | 7.6955 |  | 7.6955
03/08 15:00:00 | 24.4111 | 27.1244 | 26.2314 | 26.0086 | 25.8252 | 26.2554 | 23.2132 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7523 | [14 empty] | 1.4351 |  | 7.5753 |  |  |  | 7.5753 |  | 7.5753 |  | 7.5753 |  | 7.5753 |  | 7.5753
03/08 16:00:00 | 24.5791 | 27.3932 | 26.4582 | 26.2074 | 26.0089 | 26.4983 | 23.2482 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7374 | [14 empty] | 1.7713 |  | 7.4934 |  |  |  | 7.4934 |  | 7.4934 |  | 7.4934 |  | 7.4934 |  | 7.4934
03/08 17:00:00 | 24.7971 | 27.7185 | 26.765 | 26.4759 | 26.2738 | 26.8122 | 23.2653 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8288 | [14 empty] | 2.3464 |  | 8.0021 |  |  |  | 8.0021 |  | 8.0021 |  | 8.0021 |  | 8.0021 |  | 8.0021
03/08 18:00:00 | 24.9239 | 27.9337 | 26.9558 | 26.6378 | 26.4324 | 27.0167 | 23.2144 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7258 | [14 empty] | 2.9223 |  | 7.4297 |  |  |  | 7.4297 |  | 7.4297 |  | 7.4297 |  | 7.4297 |  | 7.4297
03/08 19:00:00 | 25.0015 | 28.0617 | 27.0496 | 26.7104 | 26.4887 | 27.1215 | 22.8377 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7997 | [14 empty] | 4.6823 |  | 7.8383 |  |  |  | 7.8383 |  | 7.8383 |  | 7.8383 |  | 7.8383 |  | 7.8383
03/08 20:00:00 | 24.6481 | 27.7248 | 26.7377 | 26.3631 | 26.0919 | 26.7174 | 22.4135 | 0 | 0 | 0 | 0 | 0 | 0 | 16.8935 | [14 empty] | 4.9937 |  | 285.3887 |  |  |  | 285.3887 |  | 285.3887 |  | 285.3887 |  | 285.3887 |  | 285.3887
03/08 21:00:00 | 24.1043 | 27.149 | 26.2327 | 25.8272 | 25.475 | 26.1284 | 22.3679 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8878 | [14 empty] | 3.0149 |  | 15.1148 |  |  |  | 15.1148 |  | 15.1148 |  | 15.1148 |  | 15.1148 |  | 15.1148
03/08 22:00:00 | 23.7077 | 26.7212 | 25.8595 | 25.4232 | 25.0609 | 25.7218 | 22.0995 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1489 | [14 empty] | 2.5863 |  | 9.9158 |  |  |  | 9.9158 |  | 9.9158 |  | 9.9158 |  | 9.9158 |  | 9.9158
03/08 23:00:00 | 23.4374 | 26.3796 | 25.6051 | 25.0785 | 24.7325 | 25.3989 | 21.7047 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1131 | [14 empty] | 3.0024 |  | 9.6915 |  |  |  | 9.6915 |  | 9.6915 |  | 9.6915 |  | 9.6915 |  | 9.6915
03/08 24:00:00 | 23.2039 | 26.0475 | 25.3821 | 24.8195 | 24.4187 | 25.0902 | 21.3355 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9538 | [14 empty] | 3.4909 |  | 8.7252 |  |  |  | 8.7252 |  | 8.7252 |  | 8.7252 |  | 8.7252 |  | 8.7252
03/09 01:00:00 | 22.9797 | 25.7837 | 25.2133 | 24.5854 | 24.1726 | 24.848 | 21.0138 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8913 | [14 empty] | 3.8648 |  | 8.3596 |  |  |  | 8.3596 |  | 8.3596 |  | 8.3596 |  | 8.3596 |  | 8.3596
03/09 02:00:00 | 22.787 | 25.571 | 25.0706 | 24.3777 | 23.9696 | 24.6485 | 20.7133 | 27.7982 | 31.7549 | 29.8653 | 34.8287 | 38.59 | 34.6831 | 2.8647 | [14 empty] | 4.3005 |  | 621.6815 |  |  |  | 834.6469 |  | 729.033 |  | 1021.6992 |  | 1276.3031 |  | 1012.4124
03/09 03:00:00 | 23.046 | 25.751 | 25.347 | 24.6413 | 24.2561 | 24.8894 | 20.4687 | 21.7787 | 19.8486 | 21.2325 | 23.6931 | 24.7603 | 22.8852 | 2.8131 | [14 empty] | 6.6423 |  | 359.694 |  |  |  | 290.2099 |  | 339.2751 |  | 435.977 |  | 481.68 |  | 402.8886
03/09 04:00:00 | 23.277 | 25.923 | 25.5792 | 24.8618 | 24.5033 | 25.0912 | 20.2557 | 16.8998 | 18.1963 | 19.7936 | 21.8481 | 22.6152 | 21.0167 | 2.9095 | [14 empty] | 9.1282 |  | 195.7272 |  |  |  | 233.6857 |  | 285.0711 |  | 358.6695 |  | 388.3124 |  | 327.8698
03/09 05:00:00 | 23.3406 | 25.9986 | 25.6861 | 24.9528 | 24.6077 | 25.1681 | 20.0019 | 16.3212 | 17.3551 | 15.5799 | 20.6846 | 21.3944 | 19.903 | 2.9158 | [14 empty] | 11.1471 |  | 179.7025 |  |  |  | 208.4917 |  | 160.3792 |  | 315.7283 |  | 341.4553 |  | 288.5632
03/09 06:00:00 | 23.3399 | 26.0251 | 25.692 | 24.9739 | 24.6353 | 25.176 | 19.7461 | 16.1829 | 16.6924 | 15.4719 | 17.6249 | 20.7778 | 19.3582 | 2.9303 | [14 empty] | 12.915 |  | 175.6319 |  |  |  | 189.3953 |  | 157.2931 |  | 215.9313 |  | 318.535 |  | 269.8771
03/09 07:00:00 | 23.3158 | 26.0083 | 25.6583 | 24.9323 | 24.6014 | 25.1267 | 19.5001 | 15.5849 | 16.0873 | 18.262 | 19.7303 | 19.8543 | 18.5175 | 14.6488 | [14 empty] | 14.5598 |  | 0.87638 |  |  |  | 2.0694 |  | 13.0554 |  | 25.8216 |  | 27.0975 |  | 14.9667
03/09 08:00:00 | 23.2656 | 25.9422 | 25.6101 | 24.8521 | 24.5058 | 25.0204 | 20.2444 | 18.5141 | 18.4176 | 21.5184 | 21.4873 | 25.5154 | 21.0522 | 78.8099 | [14 empty] | 9.128 |  | 3635.5818 |  |  |  | 3647.2305 |  | 3282.3148 |  | 3285.8881 |  | 2840.3042 |  | 3335.9597
03/09 09:00:00 | 23.2108 | 25.8726 | 25.5304 | 24.7522 | 24.4305 | 24.9265 | 22.1338 | 19.0497 | 19.2062 | 19.1593 | 21.0163 | 21.2846 | 20.0394 | 16.9476 | [14 empty] | 1.16 |  | 4.4189 |  |  |  | 5.1014 |  | 4.8918 |  | 16.5545 |  | 18.8097 |  | 9.5593
03/09 10:00:00 | 23.371 | 25.9857 | 25.6289 | 24.8439 | 24.5395 | 25.0581 | 22.9064 | 16.7233 | 15.796 | 16.9559 | 18.3317 | 18.6574 | 17.2131 | 3.057 | [14 empty] | 0.21591 |  | 186.7681 |  |  |  | 162.2815 |  | 193.18 |  | 233.3153 |  | 243.3739 |  | 200.3958
03/09 11:00:00 | 24.0051 | 26.7181 | 26.2481 | 25.3871 | 25.1634 | 25.7691 | 23.2161 | 14.5264 | 10.5985 | 14.5506 | 16.0054 | 16.2939 | 14.93 | 3.4275 | [14 empty] | 0.62249 |  | 123.1864 |  |  |  | 51.4245 |  | 123.7236 |  | 158.2056 |  | 165.5446 |  | 132.309
03/09 12:00:00 | 24.8712 | 27.724 | 27.1104 | 26.1443 | 26.0017 | 26.6349 | 23.5232 | 13.5731 | 7.3869 | 13.0595 | 14.9095 | 15.2393 | 13.8566 | 3.0473 | [14 empty] | 1.8173 |  | 110.7941 |  |  |  | 18.8329 |  | 100.2447 |  | 140.7135 |  | 148.6458 |  | 116.841
03/09 13:00:00 | 25.3982 | 28.3187 | 27.6595 | 26.6772 | 26.5735 | 27.2112 | 23.7451 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8883 | [14 empty] | 2.7329 |  | 8.3424 |  |  |  | 8.3424 |  | 8.3424 |  | 8.3424 |  | 8.3424 |  | 8.3424
03/09 14:00:00 | 25.1801 | 28.2088 | 27.4567 | 26.5355 | 26.4572 | 27.096 | 23.8976 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8425 | [14 empty] | 1.6449 |  | 8.0796 |  |  |  | 8.0796 |  | 8.0796 |  | 8.0796 |  | 8.0796 |  | 8.0796
03/09 15:00:00 | 24.9797 | 28.1095 | 27.3074 | 26.3937 | 26.3348 | 26.9937 | 24.0612 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3942 | [14 empty] | 0.84367 |  | 1.9438 |  |  |  | 1.9438 |  | 1.9438 |  | 1.9438 |  | 1.9438 |  | 1.9438
03/09 16:00:00 | 25.2288 | 28.4183 | 27.621 | 26.6787 | 26.6298 | 27.3275 | 24.2959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.87039 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/09 17:00:00 | 25.5032 | 28.73 | 27.9202 | 26.9614 | 26.9209 | 27.6511 | 24.3611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.3044 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/09 18:00:00 | 25.6539 | 28.9314 | 28.0716 | 27.1054 | 27.0576 | 27.8237 | 24.1838 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89294 | [14 empty] | 2.1612 |  | 0.79734 |  |  |  | 0.79734 |  | 0.79734 |  | 0.79734 |  | 0.79734 |  | 0.79734
03/09 19:00:00 | 25.6335 | 28.9638 | 28.0209 | 27.0802 | 27.0191 | 27.8036 | 23.7561 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9082 | [14 empty] | 3.5246 |  | 15.2743 |  |  |  | 15.2743 |  | 15.2743 |  | 15.2743 |  | 15.2743 |  | 15.2743
03/09 20:00:00 | 25.0485 | 28.2823 | 27.3567 | 26.4655 | 26.3689 | 27.1214 | 23.0752 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0141 | [14 empty] | 3.8941 |  | 49.1977 |  |  |  | 49.1977 |  | 49.1977 |  | 49.1977 |  | 49.1977 |  | 49.1977
03/09 21:00:00 | 24.3473 | 27.57 | 26.7313 | 25.7933 | 25.6394 | 26.4347 | 22.5739 | 16.0269 | 17.7692 | 16.8137 | 18.9236 | 20.3188 | 18.4562 | 10.12 | [14 empty] | 3.1451 |  | 34.8916 |  |  |  | 58.5099 |  | 44.8053 |  | 77.5032 |  | 104.0164 |  | 69.4928
03/09 22:00:00 | 24.1027 | 27.2684 | 26.5201 | 25.5461 | 25.3796 | 26.1526 | 22.1175 | 12.6012 | 11.2208 | 11.9486 | 12.8758 | 13.0406 | 12.1948 | 13.2259 | [14 empty] | 3.941 |  | 0.39017 |  |  |  | 4.0203 |  | 1.6314 |  | 0.12254 |  | 0.034327 |  | 1.0631
03/09 23:00:00 | 23.9832 | 27.0739 | 26.3486 | 25.3734 | 25.227 | 25.9737 | 21.5658 | 13.214 | 10.773 | 12.0839 | 13.276 | 13.3088 | 12.6032 | 16.3317 | [14 empty] | 5.8438 |  | 9.7204 |  |  |  | 30.8992 |  | 18.0438 |  | 9.3375 |  | 9.138 |  | 13.9017
03/09 24:00:00 | 23.6981 | 26.6886 | 26.0125 | 25.0262 | 24.8491 | 25.5676 | 20.9527 | 12.2791 | 10.6394 | 11.5683 | 12.4026 | 12.4788 | 11.7931 | 19.4376 | [14 empty] | 7.5376 |  | 51.2449 |  |  |  | 77.4092 |  | 61.9269 |  | 49.491 |  | 48.4246 |  | 58.4382
03/10 01:00:00 | 23.3385 | 26.2533 | 25.594 | 24.6082 | 24.4131 | 25.1135 | 20.3116 | 12.3953 | 10.5334 | 11.5532 | 12.4954 | 12.5357 | 11.9349 | 22.5435 | [14 empty] | 9.1616 |  | 102.9854 |  |  |  | 144.2433 |  | 120.7856 |  | 100.9635 |  | 100.1553 |  | 112.5432
03/10 02:00:00 | 22.9725 | 25.8556 | 25.1795 | 24.184 | 23.9916 | 24.698 | 19.7837 | 11.9697 | 10.3794 | 11.2522 | 12.1309 | 12.1924 | 11.5975 | 25.6494 | [14 empty] | 10.1686 |  | 187.1324 |  |  |  | 233.1725 |  | 207.279 |  | 182.7504 |  | 181.0911 |  | 197.4548
03/10 03:00:00 | 22.6799 | 25.4569 | 24.8545 | 23.7689 | 23.5741 | 24.2855 | 19.3829 | 11.8346 | 10.2363 | 11.1074 | 11.987 | 12.0813 | 11.4954 | 28.7552 | [14 empty] | 10.87 |  | 286.3095 |  |  |  | 342.9506 |  | 311.4458 |  | 281.1737 |  | 278.0205 |  | 297.9013
03/10 04:00:00 | 22.4071 | 25.0685 | 24.5548 | 23.4505 | 23.1879 | 23.896 | 19.3789 | 10.9887 | 9.9137 | 10.5409 | 11.1422 | 11.232 | 10.6978 | 31.8611 | [14 empty] | 9.1705 |  | 435.6593 |  |  |  | 481.6882 |  | 454.553 |  | 429.2725 |  | 425.562 |  | 447.8879
03/10 05:00:00 | 22.1419 | 24.77 | 24.2627 | 23.1617 | 22.8899 | 23.6042 | 19.2927 | 10.4171 | 9.5862 | 10.0738 | 10.5705 | 10.6721 | 10.154 | 34.967 | [14 empty] | 8.1181 |  | 602.6969 |  |  |  | 644.1846 |  | 619.6723 |  | 595.19 |  | 590.2422 |  | 615.6828
03/10 06:00:00 | 21.8795 | 24.5032 | 23.9766 | 22.8759 | 22.6144 | 23.3342 | 19.1964 | 10.2509 | 9.349 | 9.8743 | 10.4054 | 10.4912 | 9.9989 | 38.0729 | [14 empty] | 7.1992 |  | 774.0653 |  |  |  | 825.0635 |  | 795.1618 |  | 765.4896 |  | 760.7511 |  | 788.1506
03/10 07:00:00 | 21.6166 | 24.2322 | 23.6952 | 22.5896 | 22.3342 | 23.0596 | 19.0766 | 9.8566 | 9.1329 | 9.5758 | 10.0208 | 10.1058 | 9.6324 | 41.1788 | [14 empty] | 6.4515 |  | 981.0771 |  |  |  | 1026.9402 |  | 998.7491 |  | 970.8157 |  | 965.5258 |  | 995.1738
03/10 08:00:00 | 21.3512 | 23.9533 | 23.4124 | 22.2995 | 22.0443 | 22.7762 | 19.5205 | 13.4284 | 11.451 | 11.4073 | 11.5479 | 13.9958 | 10.9944 | 44.2846 | [14 empty] | 3.3514 |  | 952.1066 |  |  |  | 1078.0451 |  | 1080.9205 |  | 1071.6935 |  | 917.4139 |  | 1108.2431
03/10 09:00:00 | 21.107 | 23.6824 | 23.1442 | 22.0208 | 21.7668 | 22.5014 | 20.8567 | 36.2663 | 10.923 | 10.9356 | 13.4064 | 36.8304 | 10.4736 | 47.3905 | [14 empty] | 0.062656 |  | 123.7484 |  |  |  | 1329.8822 |  | 1328.9578 |  | 1154.9176 |  | 111.5164 |  | 1362.86
03/10 10:00:00 | 21.2565 | 23.5202 | 23.0024 | 21.8679 | 21.8293 | 22.3434 | 21.9991 | 41.245 | 10.3701 | 10.3767 | 31.5271 | 45.9646 | 9.8947 | 50.4964 | [14 empty] | 0.55144 |  | 85.5889 |  |  |  | 1610.1231 |  | 1609.5867 |  | 359.8355 |  | 20.5375 |  | 1648.4949
03/10 11:00:00 | 22.1238 | 23.5214 | 23.032 | 22.0535 | 22.7955 | 22.3467 | 22.3333 | 39.0184 | 9.7477 | 9.6265 | 43.5762 | 32.2612 | 9.0873 | 53.6023 | [14 empty] | 0.04391 |  | 212.6889 |  |  |  | 1923.2236 |  | 1933.8659 |  | 100.522 |  | 455.4415 |  | 1981.5826
03/10 12:00:00 | 23.0139 | 23.6396 | 23.1665 | 23.0026 | 24.1648 | 22.4559 | 22.4372 | 33.5272 | 8.3483 | 8.2017 | 30.8096 | 26.0614 | 7.3766 | 56.7081 | [14 empty] | 0.33254 |  | 537.3556 |  |  |  | 2338.6792 |  | 2352.8759 |  | 670.7332 |  | 939.2233 |  | 2433.6049
03/10 13:00:00 | 23.9005 | 23.9503 | 23.4462 | 24.4961 | 24.7947 | 22.723 | 22.212 | 30.7024 | 7.4306 | 7.4674 | 26.2776 | 25.0326 | 6.7541 | 37.7349 | [14 empty] | 2.8511 |  | 49.455 |  |  |  | 918.3452 |  | 916.1158 |  | 131.2683 |  | 161.3477 |  | 959.8079
03/10 14:00:00 | 24.1679 | 23.9291 | 23.3607 | 24.9233 | 24.8273 | 22.661 | 22.3307 | 28.9153 | 7.087 | 6.3719 | 25.0717 | 23.7168 | 6.6055 | 4.1627 | [14 empty] | 3.3753 |  | 612.6939 |  |  |  | 8.5516 |  | 4.8806 |  | 437.188 |  | 382.3641 |  | 5.9674
03/10 15:00:00 | 24.1716 | 23.8216 | 23.2189 | 24.8655 | 24.778 | 22.5468 | 22.2487 | 26.6324 | 6.3915 | 6.5236 | 22.821 | 21.5376 | 5.5124 | 38.2801 | [14 empty] | 3.6974 |  | 135.6693 |  |  |  | 1016.8816 |  | 1008.4727 |  | 238.9848 |  | 280.3102 |  | 1073.7205
03/10 16:00:00 | 24.6095 | 24.185 | 23.5834 | 25.192 | 25.1247 | 22.9129 | 22.2296 | 25.2816 | 5.8181 | 6.1442 | 21.8055 | 20.4495 | 5.4831 | 31.9098 | [14 empty] | 5.6639 |  | 43.9333 |  |  |  | 680.778 |  | 663.8678 |  | 102.0971 |  | 131.3393 |  | 698.3722
03/10 17:00:00 | 24.8704 | 24.4728 | 23.8339 | 25.3781 | 25.3264 | 23.1811 | 22.2602 | 24.7621 | 5.9555 | 6.4096 | 21.2244 | 19.9846 | 5.9247 | 33.0524 | [14 empty] | 6.8134 |  | 68.7288 |  |  |  | 734.244 |  | 709.8401 |  | 139.9012 |  | 170.7689 |  | 735.9131
03/10 18:00:00 | 24.7633 | 24.4035 | 23.7313 | 25.2542 | 25.1737 | 23.0779 | 22.1734 | 23.8032 | 6.0738 | 6.4718 | 20.3139 | 19.2333 | 5.9969 | 35.2272 | [14 empty] | 6.7076 |  | 130.5077 |  |  |  | 849.9199 |  | 826.8727 |  | 222.4064 |  | 255.8063 |  | 854.4132
03/10 19:00:00 | 24.5187 | 24.1558 | 23.4223 | 24.9589 | 24.8652 | 22.8105 | 22.0877 | 24.0694 | 6.8958 | 7.5511 | 20.6619 | 19.6855 | 7.4195 | 39.0111 | [14 empty] | 5.9097 |  | 223.253 |  |  |  | 1031.3892 |  | 989.7309 |  | 336.6915 |  | 373.478 |  | 998.0254
03/10 20:00:00 | 23.9218 | 23.4727 | 22.7362 | 24.2642 | 24.1384 | 22.1022 | 22.0025 | 23.5509 | 7.4054 | 7.9734 | 20.286 | 19.397 | 24.7512 | 41.374 | [14 empty] | 3.6837 |  | 317.6643 |  |  |  | 1153.8704 |  | 1115.6032 |  | 444.7055 |  | 482.9922 |  | 276.3203
03/10 21:00:00 | 23.2808 | 22.7209 | 21.9988 | 23.5176 | 23.3572 | 21.4432 | 21.7061 | 18.8734 | 6.1959 | 6.7831 | 15.9942 | 15.3058 | 18.1652 | 5.0778 | [14 empty] | 2.4795 |  | 190.3206 |  |  |  | 1.2502 |  | 2.9083 |  | 119.1693 |  | 104.6124 |  | 171.2807
03/10 22:00:00 | 22.8129 | 22.158 | 21.4808 | 22.9451 | 22.7529 | 21.2434 | 20.7676 | 17.8329 | 6.1567 | 6.5869 | 15.1765 | 14.5607 | 12.5128 | 3.7939 | [14 empty] | 4.1837 |  | 197.0919 |  |  |  | 5.5825 |  | 7.8008 |  | 129.5632 |  | 115.9236 |  | 76.018
03/10 23:00:00 | 22.4003 | 21.6564 | 21.0171 | 22.4319 | 22.2089 | 20.9362 | 19.8206 | 17.3373 | 6.1604 | 6.574 | 14.7652 | 14.1751 | 12.9775 | 9.4738 | [14 empty] | 6.6549 |  | 61.8344 |  |  |  | 10.9789 |  | 8.4085 |  | 27.999 |  | 22.1022 |  | 12.2759
03/10 24:00:00 | 21.9447 | 21.182 | 20.5893 | 21.9498 | 21.6668 | 20.5798 | 19.2598 | 17.0057 | 6.1918 | 6.6196 | 14.6129 | 14.0735 | 13.0108 | 22.223 | [14 empty] | 7.2086 |  | 27.2203 |  |  |  | 257.0019 |  | 243.4671 |  | 57.9148 |  | 66.4148 |  | 84.8662
03/11 01:00:00 | 21.5094 | 20.8091 | 20.2559 | 21.482 | 21.1596 | 20.2796 | 19.0186 | 16.2825 | 6.174 | 6.5096 | 14.0323 | 13.5461 | 12.5013 | 21.3237 | [14 empty] | 6.2045 |  | 25.4131 |  |  |  | 229.5115 |  | 219.4575 |  | 53.1645 |  | 60.4912 |  | 77.8342
03/11 02:00:00 | 21.1244 | 20.4642 | 19.9314 | 21.1065 | 20.6788 | 19.9727 | 18.8178 | 16.3133 | 6.2411 | 6.6971 | 14.1483 | 13.675 | 12.6456 | 23.617 | [14 empty] | 5.3201 |  | 53.3439 |  |  |  | 301.9205 |  | 286.2821 |  | 89.6553 |  | 98.8424 |  | 120.3718
03/11 03:00:00 | 20.7403 | 20.1066 | 19.5944 | 20.6854 | 20.1993 | 19.6472 | 18.6659 | 16.2685 | 6.3547 | 6.8637 | 14.2089 | 13.7519 | 12.7013 | 24.5474 | [14 empty] | 4.3031 |  | 68.5406 |  |  |  | 330.9746 |  | 312.7138 |  | 106.8863 |  | 116.5431 |  | 140.3319
03/11 04:00:00 | 20.3549 | 19.7401 | 19.2479 | 20.1864 | 19.7232 | 19.301 | 18.5356 | 15.7585 | 6.3745 | 6.832 | 13.8037 | 13.3937 | 12.385 | 25.864 | [14 empty] | 3.3098 |  | 102.1227 |  |  |  | 379.8442 |  | 362.2175 |  | 145.4531 |  | 155.5102 |  | 181.6852
03/11 05:00:00 | 19.9746 | 19.3746 | 18.9035 | 19.8066 | 19.3462 | 18.9528 | 18.4391 | 14.9824 | 6.2978 | 6.6485 | 13.1683 | 12.7859 | 11.8099 | 25.8308 | [14 empty] | 2.3578 |  | 117.6874 |  |  |  | 381.5367 |  | 367.9621 |  | 160.3376 |  | 170.17 |  | 196.5852
03/11 06:00:00 | 19.6001 | 19.0096 | 18.5601 | 19.4502 | 18.9839 | 18.6031 | 18.2947 | 14.2129 | 6.1531 | 7.0128 | 12.492 | 12.1368 | 11.2134 | 28.0342 | [14 empty] | 1.704 |  | 191.0268 |  |  |  | 478.7834 |  | 441.897 |  | 241.5587 |  | 252.7275 |  | 282.9379
03/11 07:00:00 | 19.2408 | 18.6565 | 18.2331 | 19.0974 | 18.6224 | 18.2656 | 18.1821 | 13.949 | 6.108 | 25.9119 | 12.3146 | 11.9645 | 32.326 | 28.9256 | [14 empty] | 1.1207 |  | 224.2966 |  |  |  | 520.6415 |  | 9.0822 |  | 275.9232 |  | 287.6786 |  | 11.5627
03/11 08:00:00 | 18.881 | 18.3022 | 18.0777 | 18.73 | 18.24 | 18.0944 | 18.2978 | 12.8939 | 26.5644 | 40.3522 | 11.3615 | 32.5891 | 45.6503 | 26.234 | [14 empty] | 0.34011 |  | 177.9574 |  |  |  | 0.1092 |  | 199.3249 |  | 221.1901 |  | 40.3875 |  | 376.9928
03/11 09:00:00 | 18.535 | 18.1048 | 18.3829 | 18.3656 | 18.0419 | 18.3382 | 18.9946 | 12.3012 | 56.1973 | 53.2581 | 11.1995 | 64.0808 | 61.7214 | 89.3507 | [14 empty] | 0.21119 |  | 5936.6342 |  |  |  | 1099.1497 |  | 1302.6744 |  | 6107.6206 |  | 638.5697 |  | 763.3775
03/11 10:00:00 | 18.3182 | 18.8696 | 19.1055 | 18.1493 | 19.0823 | 19.8511 | 20.3045 | 36.6031 | 52.3511 | 52.6875 | 42.6054 | 58.786 | 53.7393 | 29.0866 | [14 empty] | 3.9453 |  | 56.4967 |  |  |  | 541.2342 |  | 557.0003 |  | 182.7562 |  | 882.0497 |  | 607.7515
03/11 11:00:00 | 18.3692 | 20.6189 | 20.5375 | 18.2309 | 20.6396 | 21.4554 | 20.7904 | 48.482 | 39.3045 | 47.1345 | 57.0921 | 44.2298 | 43.8475 | 20.1594 | [14 empty] | 5.8622 |  | 802.171 |  |  |  | 366.5345 |  | 727.6546 |  | 1364.0245 |  | 579.3827 |  | 561.1236
03/11 12:00:00 | 19.2484 | 22.4673 | 22.0791 | 19.6738 | 21.9927 | 22.5287 | 20.8864 | 49.7705 | 34.0361 | 41.8145 | 50.9453 | 38.5046 | 39.5632 | 3.9102 | [14 empty] | 2.6828 |  | 2103.1646 |  |  |  | 907.5681 |  | 1436.7352 |  | 2212.2982 |  | 1196.7679 |  | 1271.1357
03/11 13:00:00 | 20.362 | 23.2073 | 22.7506 | 21.4642 | 22.586 | 23.0555 | 20.6361 | 44.5544 | 31.4207 | 37.5928 | 40.0051 | 35.2944 | 35.8251 | 38.4895 | [14 empty] | 0.075115 |  | 36.7827 |  |  |  | 49.9679 |  | 0.80411 |  | 2.2969 |  | 10.2092 |  | 7.0991
03/11 14:00:00 | 21.3996 | 23.6487 | 23.1542 | 22.6939 | 22.9037 | 23.4408 | 20.8614 | 41.5123 | 29.6455 | 35.9492 | 37.1877 | 34.2556 | 34.6271 | 4.6828 | [14 empty] | 0.28967 |  | 1356.4183 |  |  |  | 623.1387 |  | 977.5917 |  | 1056.5701 |  | 874.5548 |  | 896.6643
03/11 15:00:00 | 21.9228 | 23.929 | 23.4018 | 22.9969 | 23.1102 | 23.6959 | 20.6261 | 37.7323 | 27.7203 | 33.2437 | 34.2296 | 31.3295 | 31.586 | 38.0315 | [14 empty] | 1.6814 |  | 0.089493 |  |  |  | 106.3212 |  | 22.923 |  | 14.454 |  | 44.916 |  | 41.5437
03/11 16:00:00 | 22.1083 | 24.0887 | 23.5525 | 23.1082 | 23.2359 | 23.8443 | 20.7642 | 35.2571 | 25.883 | 30.9154 | 31.8148 | 29.1436 | 29.3688 | 24.3695 | [14 empty] | 1.8065 |  | 118.5414 |  |  |  | 2.2909 |  | 42.849 |  | 55.4324 |  | 22.7927 |  | 24.9935
03/11 17:00:00 | 22.1988 | 24.1956 | 23.653 | 23.1793 | 23.3085 | 23.9412 | 20.826 | 32.8475 | 24.1692 | 28.7637 | 29.4199 | 27.0001 | 27.1714 | 12.7166 | [14 empty] | 1.8848 |  | 405.2515 |  |  |  | 131.1612 |  | 257.5088 |  | 278.999 |  | 204.0176 |  | 208.9413
03/11 18:00:00 | 22.2743 | 24.2833 | 23.7429 | 23.2442 | 23.3641 | 24.0193 | 20.8122 | 29.8287 | 22.1616 | 26.1851 | 26.2963 | 24.0298 | 24.1454 | 54.6193 | [14 empty] | 2.1378 |  | 614.5714 |  |  |  | 1053.5001 |  | 808.5006 |  | 802.1876 |  | 935.7173 |  | 928.6569
03/11 19:00:00 | 22.3843 | 24.4204 | 23.8642 | 23.326 | 23.4564 | 24.1304 | 20.8461 | 30.1432 | 21.7403 | 26.1083 | 26.5621 | 24.5488 | 24.6994 | 38.8619 | [14 empty] | 2.366 |  | 76.0157 |  |  |  | 293.151 |  | 162.6555 |  | 151.2863 |  | 204.8647 |  | 200.5758
03/11 20:00:00 | 22.3381 | 24.3246 | 23.7873 | 23.1767 | 23.295 | 23.9502 | 20.5831 | 24.4752 | 16.7057 | 20.3838 | 21.0504 | 19.5321 | 19.7706 | 5.0979 | [14 empty] | 3.0802 |  | 375.4791 |  |  |  | 134.7407 |  | 233.6585 |  | 254.4835 |  | 208.3447 |  | 215.2881
03/11 21:00:00 | 22.1825 | 24.0308 | 23.5715 | 22.8755 | 22.8883 | 23.5636 | 19.6751 | 24.3211 | 16.6139 | 20.1605 | 21.0116 | 19.611 | 19.8458 | 11.3649 | [14 empty] | 6.2868 |  | 167.8643 |  |  |  | 27.5516 |  | 77.3631 |  | 93.0584 |  | 67.9983 |  | 71.9264
03/11 22:00:00 | 21.9457 | 23.6327 | 23.2779 | 22.4658 | 22.3665 | 23.0702 | 19.1172 | 24.0579 | 16.5003 | 19.9804 | 21.0068 | 19.7106 | 19.9177 | 22.0182 | [14 empty] | 8.0002 |  | 4.1605 |  |  |  | 30.4467 |  | 4.1525 |  | 1.0229 |  | 5.325 |  | 4.4121
03/11 23:00:00 | 21.6066 | 23.1053 | 22.9286 | 21.9286 | 21.8011 | 22.5134 | 18.8009 | 23.6905 | 16.343 | 19.7213 | 20.9048 | 19.6612 | 19.854 | 24.3743 | [14 empty] | 7.8723 |  | 0.46754 |  |  |  | 64.5022 |  | 21.6502 |  | 12.0374 |  | 22.2127 |  | 20.4331
03/11 24:00:00 | 21.3018 | 22.6352 | 22.5441 | 21.452 | 21.2 | 21.9427 | 18.6006 | 22.6899 | 15.9811 | 19.0789 | 20.109 | 18.9703 | 19.1945 | 25.5659 | [14 empty] | 7.2963 |  | 8.2716 |  |  |  | 91.8692 |  | 42.0818 |  | 29.7774 |  | 43.502 |  | 40.5952
03/12 01:00:00 | 21.0007 | 22.161 | 22.1479 | 20.9608 | 20.6405 | 21.5104 | 18.4847 | 22.6559 | 15.733 | 18.8972 | 20.2153 | 19.1238 | 19.3079 | 26.0339 | [14 empty] | 6.3305 |  | 11.4105 |  |  |  | 106.1076 |  | 50.932 |  | 33.8561 |  | 47.7496 |  | 45.2393
03/12 02:00:00 | 20.6748 | 21.6816 | 21.7458 | 20.5503 | 20.1745 | 21.0895 | 18.4211 | 21.2399 | 15.2823 | 17.9886 | 19.0038 | 18.0265 | 18.1574 | 27.6296 | [14 empty] | 5.0794 |  | 40.8284 |  |  |  | 152.4558 |  | 92.95 |  | 74.4042 |  | 92.2197 |  | 89.7221
03/12 03:00:00 | 20.3544 | 21.3456 | 21.4411 | 20.1577 | 19.7891 | 20.6763 | 18.3493 | 20.4231 | 14.8077 | 17.3502 | 18.3071 | 17.3881 | 17.5061 | 27.9123 | [14 empty] | 4.0205 |  | 56.0891 |  |  |  | 171.7305 |  | 111.5579 |  | 92.26 |  | 110.7605 |  | 108.2891
03/12 04:00:00 | 20.024 | 21.0141 | 21.1434 | 19.7543 | 19.3909 | 20.2566 | 18.3077 | 19.4309 | 14.3193 | 16.637 | 17.4463 | 16.5942 | 16.6928 | 27.6177 | [14 empty] | 2.9454 |  | 67.0227 |  |  |  | 176.846 |  | 120.5762 |  | 103.4563 |  | 121.5168 |  | 119.3532
03/12 05:00:00 | 19.6975 | 20.6875 | 20.8434 | 19.4319 | 19.0633 | 19.9213 | 18.3012 | 18.8096 | 13.8536 | 16.107 | 16.9266 | 16.1198 | 16.2177 | 27.7582 | [14 empty] | 1.9499 |  | 80.0769 |  |  |  | 193.3365 |  | 135.7504 |  | 117.3215 |  | 135.4515 |  | 133.181
03/12 06:00:00 | 19.387 | 20.3947 | 20.5489 | 19.1326 | 18.7538 | 19.6091 | 18.3309 | 15.1689 | 11.6045 | 13.0939 | 16.0089 | 15.2663 | 15.3528 | 27.2409 | [14 empty] | 1.1153 |  | 145.7319 |  |  |  | 244.4971 |  | 200.1358 |  | 126.158 |  | 143.391 |  | 141.3254
03/12 07:00:00 | 19.1423 | 20.1644 | 20.3146 | 18.8427 | 18.4512 | 19.3061 | 18.3414 | 14.987 | 13.3619 | 15.3322 | 15.5692 | 14.8736 | 14.9659 | 27.5945 | [14 empty] | 0.64144 |  | 158.9489 |  |  |  | 202.5654 |  | 150.3646 |  | 144.6067 |  | 161.8207 |  | 159.4822
03/12 08:00:00 | 18.951 | 19.929 | 20.0855 | 18.5369 | 18.1286 | 18.9877 | 18.7774 | 14.2603 | 10.8913 | 12.2133 | 13.2989 | 12.8904 | 12.8732 | 84.1833 | [14 empty] | 0.030113 |  | 4889.236 |  |  |  | 5371.7225 |  | 5179.685 |  | 5024.602 |  | 5082.6871 |  | 5085.1328
03/12 09:00:00 | 18.7652 | 19.687 | 19.8393 | 18.2995 | 17.8803 | 18.7453 | 20.0527 | 16.6208 | 18.8494 | 19.8024 | 15.6749 | 51.6752 | 42.8927 | 48.0612 | [14 empty] | 1.6578 |  | 988.5004 |  |  |  | 853.3317 |  | 798.5608 |  | 1048.8736 |  | 13.0614 |  | 26.7129
03/12 10:00:00 | 18.6036 | 19.5195 | 19.6762 | 18.1545 | 17.9666 | 18.7435 | 20.7646 | 40.5352 | 46.9189 | 36.6888 | 46.9238 | 61.777 | 61.1501 | 29.9291 | [14 empty] | 4.67 |  | 112.4891 |  |  |  | 288.6532 |  | 45.6933 |  | 288.8177 |  | 1014.2884 |  | 974.7472
03/12 11:00:00 | 18.7087 | 19.7967 | 19.7976 | 18.3341 | 19.3768 | 20.0409 | 20.8905 | 52.0584 | 45.9358 | 43.6974 | 60.898 | 61.2856 | 53.3843 | 27.6092 | [14 empty] | 4.7603 |  | 597.7661 |  |  |  | 335.8672 |  | 258.832 |  | 1108.1474 |  | 1134.1029 |  | 664.3603
03/12 12:00:00 | 19.2159 | 21.0276 | 20.2622 | 19.4729 | 21.1051 | 21.6756 | 20.9459 | 52.7944 | 34.5748 | 44.1769 | 59.1245 | 47.7436 | 43.0606 | 4.5384 | [14 empty] | 2.9932 |  | 2328.6391 |  |  |  | 902.1807 |  | 1571.2091 |  | 2979.6385 |  | 1866.685 |  | 1483.9601
03/12 13:00:00 | 19.7638 | 22.0907 | 20.9042 | 21.0965 | 22.1924 | 22.4583 | 20.8661 | 48.0957 | 30.1111 | 37.457 | 47.6031 | 41.5926 | 38.3078 | 34.5684 | [14 empty] | 1.2151 |  | 182.9881 |  |  |  | 19.8675 |  | 8.3444 |  | 169.9051 |  | 49.3402 |  | 13.9833
03/12 14:00:00 | 20.481 | 22.5378 | 21.6556 | 22.2816 | 22.558 | 22.7652 | 20.9022 | 45.0611 | 28.4456 | 33.9039 | 41.8194 | 38.8675 | 35.7305 | 20.5255 | [14 empty] | 0.17743 |  | 601.997 |  |  |  | 62.7283 |  | 178.9804 |  | 453.4276 |  | 336.429 |  | 231.1918
03/12 15:00:00 | 21.0257 | 22.7294 | 22.037 | 22.7074 | 22.6966 | 22.9093 | 20.8311 | 42.1214 | 26.8157 | 32.1363 | 39.5103 | 36.6165 | 33.6616 | 17.3155 | [14 empty] | 0.037889 |  | 615.3347 |  |  |  | 90.2546 |  | 219.656 |  | 492.6121 |  | 372.528 |  | 267.1946
03/12 16:00:00 | 21.2563 | 22.8142 | 22.1471 | 22.7927 | 22.7425 | 22.966 | 20.7801 | 38.9452 | 25.2584 | 25.9115 | 36.6714 | 34.0189 | 31.275 | 28.5436 | [14 empty] | 0.22674 |  | 108.1927 |  |  |  | 10.7924 |  | 6.928 |  | 66.0614 |  | 29.9789 |  | 7.4608
03/12 17:00:00 | 21.375 | 22.8638 | 22.1674 | 22.8328 | 22.7627 | 22.9911 | 20.9746 | 35.272 | 23.258 | 28.3345 | 32.8906 | 30.4941 | 27.9613 | 4.1541 | [14 empty] | 0.16028 |  | 968.3257 |  |  |  | 364.958 |  | 584.691 |  | 825.7836 |  | 693.7935 |  | 566.7797
03/12 18:00:00 | 21.4711 | 22.9173 | 22.2412 | 22.868 | 22.7871 | 23.0254 | 20.8101 | 33.6307 | 21.9058 | 26.3327 | 30.954 | 28.7123 | 26.3723 | 48.2726 | [14 empty] | 0.43684 |  | 214.3826 |  |  |  | 695.206 |  | 481.3572 |  | 299.9331 |  | 382.6035 |  | 479.6192
03/12 19:00:00 | 21.477 | 22.8884 | 22.2513 | 22.7961 | 22.6907 | 22.9299 | 20.6582 | 33.2123 | 21.5713 | 25.9826 | 30.4657 | 28.4772 | 26.4117 | 4.6838 | [14 empty] | 0.67033 |  | 813.8778 |  |  |  | 285.1883 |  | 453.6426 |  | 664.7065 |  | 566.1278 |  | 472.1022
03/12 20:00:00 | 21.2986 | 22.6113 | 22.0668 | 22.4447 | 22.3269 | 22.5567 | 19.7874 | 25.9811 | 16.3388 | 19.714 | 23.3584 | 21.8395 | 20.4684 | 25.8486 | [14 empty] | 2.2838 |  | 0.017536 |  |  |  | 90.4374 |  | 37.6336 |  | 6.2015 |  | 16.0735 |  | 28.9471
03/12 21:00:00 | 21.0753 | 22.2695 | 21.8407 | 22.0373 | 21.8563 | 22.1251 | 19.2759 | 24.2311 | 15.7849 | 18.7287 | 21.8237 | 20.474 | 19.1462 | 20.1528 | [14 empty] | 3.2377 |  | 16.6329 |  |  |  | 19.0781 |  | 2.0281 |  | 2.7918 |  | 0.10319 |  | 1.0132
03/12 22:00:00 | 20.8674 | 21.9192 | 21.5949 | 21.6099 | 21.3305 | 21.6729 | 19.037 | 23.1114 | 15.2723 | 17.9182 | 20.9077 | 19.6735 | 18.418 | 22.5733 | [14 empty] | 3.3506 |  | 0.2895 |  |  |  | 53.3042 |  | 21.6697 |  | 2.7742 |  | 8.409 |  | 17.2665
03/12 23:00:00 | 20.6364 | 21.4876 | 21.3393 | 21.1055 | 20.8169 | 21.2151 | 18.8834 | 22.4691 | 14.9216 | 17.4603 | 20.4739 | 19.2839 | 18.0716 | 22.6702 | [14 empty] | 3.0727 |  | 0.040445 |  |  |  | 60.0395 |  | 27.1431 |  | 4.8237 |  | 11.4668 |  | 21.1468
03/12 24:00:00 | 20.3767 | 21.1172 | 21.0786 | 20.6714 | 20.2767 | 20.7481 | 18.7425 | 21.6715 | 14.5611 | 16.9413 | 19.8236 | 18.7347 | 17.5694 | 24.0377 | [14 empty] | 2.6708 |  | 5.5992 |  |  |  | 89.8066 |  | 50.3592 |  | 17.7591 |  | 28.1221 |  | 41.8388
03/13 01:00:00 | 20.0964 | 20.7444 | 20.7981 | 20.2089 | 19.8215 | 20.355 | 18.6273 | 21.3042 | 14.3023 | 16.7094 | 19.6043 | 18.5469 | 17.3976 | 25.5926 | [14 empty] | 2.1583 |  | 18.3902 |  |  |  | 127.4718 |  | 78.9113 |  | 35.8596 |  | 49.6427 |  | 67.1584
03/13 02:00:00 | 19.7887 | 20.3575 | 20.4518 | 19.8032 | 19.3375 | 19.9128 | 18.5599 | 20.7608 | 14.0099 | 16.3107 | 19.1617 | 18.1861 | 17.0932 | 26.4778 | [14 empty] | 1.5098 |  | 32.684 |  |  |  | 155.45 |  | 103.37 |  | 53.5262 |  | 68.7529 |  | 88.0714
03/13 03:00:00 | 19.4806 | 20.0484 | 20.1252 | 19.4066 | 18.9518 | 19.5037 | 18.4026 | 20.0245 | 13.6287 | 15.8285 | 18.5035 | 17.6103 | 16.5728 | 28.4409 | [14 empty] | 1.1621 |  | 70.8357 |  |  |  | 219.4015 |  | 159.0748 |  | 98.7535 |  | 117.3018 |  | 140.8516
03/13 04:00:00 | 19.176 | 19.7624 | 19.834 | 19.0891 | 18.5672 | 19.1169 | 18.3068 | 19.0108 | 13.1987 | 15.1638 | 17.6097 | 16.7643 | 15.7722 | 28.7972 | [14 empty] | 0.75546 |  | 95.7751 |  |  |  | 243.3161 |  | 185.8716 |  | 125.1621 |  | 144.7906 |  | 169.6528
03/13 05:00:00 | 18.881 | 19.4771 | 19.5539 | 18.786 | 18.2573 | 18.8126 | 18.2613 | 18.4252 | 12.8099 | 14.7025 | 17.0829 | 35.4959 | 15.3474 | 29.145 | [14 empty] | 0.38407 |  | 114.9139 |  |  |  | 266.8365 |  | 208.5863 |  | 145.4938 |  | 40.3339 |  | 190.3726
03/13 06:00:00 | 18.5957 | 19.1939 | 19.28 | 18.4809 | 18.12 | 18.5261 | 18.2334 | 14.8707 | 12.4111 | 12.0155 | 16.2787 | 47.3178 | 14.6401 | 28.9492 | [14 empty] | 0.13129 |  | 198.206 |  |  |  | 273.5094 |  | 286.7508 |  | 160.542 |  | 337.404 |  | 204.7502
03/13 07:00:00 | 18.3575 | 18.9115 | 19.055 | 18.1718 | 18.336 | 18.2326 | 18.5911 | 14.2531 | 11.9178 | 11.7358 | 33.3908 | 46.5316 | 33.3795 | 79.1222 | [14 empty] | 0.054569 |  | 4208.0055 |  |  |  | 4516.4297 |  | 4540.9226 |  | 2091.3648 |  | 1062.147 |  | 2092.391
03/13 08:00:00 | 18.1752 | 18.6149 | 18.8809 | 18.0212 | 18.6513 | 18.0948 | 19.7789 | 39.7547 | 37.2229 | 39.1117 | 60.762 | 62.7102 | 62.2002 | 65.462 | [14 empty] | 2.572 |  | 660.866 |  |  |  | 797.4478 |  | 694.3365 |  | 22.0901 |  | 7.5722 |  | 10.6396
03/13 09:00:00 | 18.3429 | 18.6553 | 19.0132 | 19.0099 | 20.6152 | 19.411 | 21.05 | 49.9499 | 53.9498 | 51.008 | 57.2815 | 56.7263 | 57.4067 | 63.8515 | [14 empty] | 7.3283 |  | 193.2535 |  |  |  | 98.0422 |  | 164.9552 |  | 43.164 |  | 50.7687 |  | 41.5346
03/13 10:00:00 | 19.1928 | 20.2651 | 20.1141 | 21.0594 | 22.5051 | 21.6295 | 22.0819 | 50.9125 | 47.7807 | 50.2766 | 54.1102 | 46.7769 | 45.9462 | 15.0199 | [14 empty] | 8.3471 |  | 1288.2766 |  |  |  | 1073.2711 |  | 1243.0336 |  | 1528.0536 |  | 1008.5082 |  | 956.4346
03/13 11:00:00 | 20.6601 | 22.986 | 22.265 | 22.9853 | 23.6982 | 23.5264 | 22.1362 | 50.817 | 36.6705 | 41.1761 | 45.7384 | 41.7099 | 39.896 | 34.3172 | [14 empty] | 2.1789 |  | 272.2442 |  |  |  | 5.5381 |  | 47.0442 |  | 130.4434 |  | 54.6521 |  | 31.1233
03/13 12:00:00 | 22.164 | 24.748 | 23.8371 | 24.1041 | 24.3263 | 24.4223 | 22.4716 | 43.3689 | 32.2692 | 36.0787 | 39.707 | 37.6055 | 35.5047 | 20.8523 | [14 empty] | 0.094603 |  | 506.9962 |  |  |  | 130.345 |  | 231.8428 |  | 355.4984 |  | 280.669 |  | 214.6931
03/13 13:00:00 | 23.0515 | 25.3975 | 24.4923 | 24.6126 | 24.7018 | 24.8386 | 22.7263 | 39.5489 | 28.207 | 32.9272 | 36.4522 | 34.295 | 32.3026 | 3.7316 | [14 empty] | 0.1057 |  | 1282.8759 |  |  |  | 599.0416 |  | 852.3834 |  | 1070.6348 |  | 934.1199 |  | 816.3021
03/13 14:00:00 | 23.5877 | 25.881 | 24.9031 | 25.0139 | 25.1027 | 25.2776 | 22.5794 | 36.5472 | 24.9391 | 30.0237 | 33.167 | 31.105 | 29.3154 | 22.4074 | [14 empty] | 1.0167 |  | 199.9345 |  |  |  | 6.4096 |  | 58.0089 |  | 115.769 |  | 75.649 |  | 47.721
03/13 15:00:00 | 24.0232 | 26.272 | 25.3019 | 25.3783 | 25.4778 | 25.673 | 22.7612 | 33.486 | 22.2598 | 27.3598 | 30.2347 | 28.3513 | 26.5841 | 13.7145 | [14 empty] | 1.5925 |  | 390.9131 |  |  |  | 73.022 |  | 186.1941 |  | 272.9179 |  | 214.2351 |  | 165.6266
03/13 16:00:00 | 24.3281 | 26.5632 | 25.6152 | 25.6484 | 25.7531 | 25.9705 | 22.7744 | 31.6337 | 21.2204 | 25.8752 | 28.5783 | 26.959 | 25.1881 | 3.3456 | [14 empty] | 2.414 |  | 800.2161 |  |  |  | 319.5067 |  | 507.5818 |  | 636.6909 |  | 557.5906 |  | 477.0947
03/13 17:00:00 | 24.511 | 26.7629 | 25.7995 | 25.8177 | 25.9161 | 26.1584 | 22.6083 | 30.1052 | 23.5876 | 25.4163 | 28.0386 | 26.6576 | 25.0057 | 43.9228 | [14 empty] | 3.6199 |  | 190.9254 |  |  |  | 413.5217 |  | 342.4905 |  | 252.3072 |  | 298.0857 |  | 357.8576
03/13 18:00:00 | 24.4882 | 26.6867 | 25.772 | 25.7446 | 25.8413 | 26.0529 | 22.6144 | 28.7845 | 23.7564 | 24.8289 | 27.2152 | 25.9988 | 24.5708 | 32.5735 | [14 empty] | 3.5112 |  | 14.3559 |  |  |  | 77.7414 |  | 59.9778 |  | 28.711 |  | 43.2267 |  | 64.043
03/13 19:00:00 | 24.2953 | 26.466 | 25.5658 | 25.4996 | 25.5917 | 25.7952 | 22.6845 | 27.9288 | 23.5547 | 24.0859 | 26.2805 | 25.0151 | 23.7949 | 32.8634 | [14 empty] | 2.5946 |  | 24.35 |  |  |  | 86.6531 |  | 77.0449 |  | 43.3347 |  | 61.5957 |  | 82.2375
03/13 20:00:00 | 24.0432 | 26.1633 | 25.2773 | 25.1875 | 25.228 | 25.4193 | 22.5283 | 27.0144 | 22.6044 | 23.2394 | 25.3132 | 24.1006 | 22.9969 | 4.73 | [14 empty] | 2.2951 |  | 496.5943 |  |  |  | 319.4943 |  | 342.5996 |  | 423.6683 |  | 375.2192 |  | 333.6802
03/13 21:00:00 | 23.7888 | 25.8757 | 24.9643 | 24.8373 | 24.8127 | 24.9984 | 21.8229 | 21.8384 | 16.6657 | 17.8821 | 19.8115 | 18.8962 | 18.1821 | 3.4919 | [14 empty] | 3.865 |  | 336.5919 |  |  |  | 173.5493 |  | 207.0774 |  | 266.3282 |  | 237.2928 |  | 215.8029
03/13 22:00:00 | 23.5178 | 25.5372 | 24.6464 | 24.4382 | 24.3565 | 24.5713 | 21.0413 | 20.947 | 16.2948 | 17.2641 | 19.046 | 18.2162 | 17.4997 | 3.2703 | [14 empty] | 6.133 |  | 312.4665 |  |  |  | 169.6371 |  | 195.827 |  | 248.8727 |  | 223.3796 |  | 202.477
03/13 23:00:00 | 23.2067 | 25.1142 | 24.3245 | 23.9678 | 23.8255 | 24.129 | 20.3341 | 20.0491 | 15.8616 | 16.66 | 18.3907 | 17.6161 | 16.9266 | 3.0903 | [14 empty] | 8.2522 |  | 287.6022 |  |  |  | 163.1075 |  | 184.1373 |  | 234.1039 |  | 210.9987 |  | 191.4445
03/13 24:00:00 | 22.9066 | 24.7586 | 24.0682 | 23.5903 | 23.3126 | 23.6844 | 19.7863 | 19.3317 | 15.4019 | 16.1757 | 17.7944 | 17.1031 | 16.4142 | 9.6328 | [14 empty] | 9.7367 |  | 94.0685 |  |  |  | 33.2826 |  | 42.8089 |  | 66.6112 |  | 55.8052 |  | 45.9872
03/14 01:00:00 | 22.6603 | 24.4374 | 23.819 | 23.2424 | 22.9234 | 23.2821 | 19.6422 | 19.8088 | 15.3675 | 16.4024 | 18.2325 | 17.5843 | 16.9411 | 14.1663 | [14 empty] | 9.1087 |  | 31.8372 |  |  |  | 1.4428 |  | 5 |  | 16.5334 |  | 11.6826 |  | 7.6991
03/14 02:00:00 | 21.9904 | 23.7007 | 23.0638 | 22.4265 | 22.0526 | 22.4887 | 19.612 | 18.2525 | 14.9329 | 15.4722 | 16.9465 | 16.3976 | 15.7255 | 17.2601 | [14 empty] | 5.6567 |  | 0.985 |  |  |  | 5.4159 |  | 3.1965 |  | 0.09834 |  | 0.74389 |  | 2.3549
03/14 03:00:00 | 21.6186 | 23.262 | 22.6891 | 21.9956 | 21.6154 | 22.0902 | 19.5591 | 14.7014 | 14.241 | 14.7593 | 16.2344 | 15.6955 | 15.061 | 16.6645 | [14 empty] | 4.2416 |  | 3.8536 |  |  |  | 5.8731 |  | 3.6298 |  | 0.18491 |  | 0.93893 |  | 2.5712
03/14 04:00:00 | 21.4858 | 23.1218 | 22.5974 | 21.8618 | 21.5049 | 21.9692 | 19.4342 | 17.5268 | 13.843 | 14.4206 | 15.9183 | 15.3968 | 14.8029 | 17.6878 | [14 empty] | 4.2089 |  | 0.025917 |  |  |  | 14.7819 |  | 10.6743 |  | 3.1309 |  | 5.2486 |  | 8.3225
03/14 05:00:00 | 21.3364 | 22.8892 | 22.4322 | 21.6141 | 21.2709 | 21.7319 | 19.3856 | 17.032 | 13.5582 | 14.1968 | 15.7569 | 15.2653 | 14.6707 | 17.9003 | [14 empty] | 3.8058 |  | 0.75393 |  |  |  | 18.8538 |  | 13.7156 |  | 4.594 |  | 6.9434 |  | 10.4302
03/14 06:00:00 | 21.1086 | 22.6278 | 22.2193 | 21.3302 | 20.9924 | 21.4557 | 19.283 | 13.8004 | 13.1366 | 11.5983 | 15.0952 | 14.6332 | 14.0864 | 19.3157 | [14 empty] | 3.3327 |  | 30.4183 |  |  |  | 38.1805 |  | 59.5578 |  | 17.8124 |  | 21.9251 |  | 27.3447
03/14 07:00:00 | 20.9091 | 22.385 | 22.0301 | 21.0651 | 20.7266 | 21.1974 | 19.6381 | 13.5667 | 12.7382 | 11.5156 | 14.6001 | 14.1656 | 13.6389 | 79.4634 | [14 empty] | 1.6155 |  | 4342.3794 |  |  |  | 4452.2626 |  | 4616.9094 |  | 4207.2479 |  | 4263.8127 |  | 4332.8734
03/14 08:00:00 | 20.7526 | 22.1339 | 21.8762 | 20.7905 | 20.4473 | 20.9299 | 20.8236 | 33.8812 | 16.3756 | 16.5975 | 38.5472 | 41.3918 | 39.2509 | 64.7264 | [14 empty] | 0.0050507 |  | 951.4261 |  |  |  | 2337.7957 |  | 2316.3884 |  | 685.3492 |  | 544.5038 |  | 648.9979
03/14 09:00:00 | 20.7837 | 21.966 | 21.7728 | 20.771 | 20.4399 | 20.9234 | 21.705 | 49.0892 | 29.9995 | 30.0697 | 57.8559 | 60.648 | 59.0201 | 47.9782 | [14 empty] | 0.84876 |  | 1.2342 |  |  |  | 323.2348 |  | 320.7144 |  | 97.5685 |  | 160.5223 |  | 121.9233
03/14 10:00:00 | 21.2073 | 21.9349 | 21.7583 | 21.6746 | 21.5661 | 21.9629 | 21.9716 | 47.4758 | 42.9766 | 40.5305 | 49.9747 | 50.663 | 49.7749 | 39.2433 | [14 empty] | 0.58423 |  | 67.7732 |  |  |  | 13.9371 |  | 1.6567 |  | 115.161 |  | 130.4095 |  | 110.9143
03/14 11:00:00 | 21.7762 | 22.3033 | 21.9804 | 23.0207 | 23.0043 | 23.4416 | 21.9191 | 45.0885 | 32.1261 | 42.9938 | 42.2188 | 41.764 | 41.4562 | 41.2601 | [14 empty] | 0.020411 |  | 14.6563 |  |  |  | 83.4314 |  | 3.0055 |  | 0.91898 |  | 0.25387 |  | 0.038443
03/14 12:00:00 | 22.114 | 23.0995 | 22.4058 | 23.6566 | 23.6314 | 23.9849 | 21.8636 | 46.4907 | 27.5374 | 37.7119 | 39.8901 | 39.5154 | 39.3127 | 39.0501 | [14 empty] | 0.062669 |  | 55.3635 |  |  |  | 132.5417 |  | 1.7908 |  | 0.70573 |  | 0.21653 |  | 0.068972
03/14 13:00:00 | 22.3225 | 23.5005 | 22.8884 | 23.7089 | 23.6866 | 24.0589 | 21.6542 | 42.7929 | 26.3065 | 33.9654 | 37.2712 | 37.0565 | 36.8008 | 37.6828 | [14 empty] | 0.44661 |  | 26.1136 |  |  |  | 129.4195 |  | 13.8183 |  | 0.16936 |  | 0.39218 |  | 0.77784
03/14 14:00:00 | 22.5323 | 23.6121 | 23.1554 | 23.7404 | 23.7119 | 24.1234 | 21.5638 | 39.8033 | 24.7195 | 32.0827 | 35.0258 | 34.8517 | 34.5447 | 34.8751 | [14 empty] | 0.93796 |  | 24.2873 |  |  |  | 103.1362 |  | 7.7978 |  | 0.022716 |  | 0.00054684 |  | 0.10915
03/14 15:00:00 | 22.6695 | 23.6947 | 23.2912 | 23.7508 | 23.7273 | 24.1773 | 21.4303 | 32.0787 | 23.3122 | 26.0007 | 32.7714 | 32.6296 | 32.3143 | 50.2899 | [14 empty] | 1.5358 |  | 331.6477 |  |  |  | 727.7946 |  | 589.9684 |  | 306.8975 |  | 311.8871 |  | 323.1226
03/14 16:00:00 | 22.6631 | 23.7203 | 23.3013 | 23.7006 | 23.6864 | 24.1729 | 21.7149 | 30.2658 | 19.4848 | 24.8791 | 30.3215 | 30.1959 | 29.8811 | 29.8753 | [14 empty] | 0.89904 |  | 0.15249 |  |  |  | 107.9609 |  | 24.9615 |  | 0.1991 |  | 0.10278 |  | 3.3809e-05
03/14 17:00:00 | 22.6314 | 23.7091 | 23.2887 | 23.624 | 23.6199 | 24.1396 | 21.6083 | 34.8865 | 21.6852 | 28.4306 | 29.2886 | 29.1397 | 28.8529 | 47.9048 | [14 empty] | 1.0467 |  | 169.4771 |  |  |  | 687.4643 |  | 379.2422 |  | 346.5643 |  | 352.1276 |  | 362.9732
03/14 18:00:00 | 22.4901 | 23.4852 | 23.1213 | 23.2745 | 23.2868 | 23.836 | 21.5727 | 31.2861 | 20.3672 | 25.8437 | 26.6485 | 26.4631 | 26.1746 | 56.7978 | [14 empty] | 0.84154 |  | 650.8494 |  |  |  | 1327.1879 |  | 958.1554 |  | 908.9849 |  | 920.1956 |  | 937.7792
03/14 19:00:00 | 22.234 | 23.1057 | 22.8491 | 22.7903 | 22.7311 | 23.3053 | 21.6853 | 29.7438 | 19.5432 | 24.6273 | 25.2701 | 25.1616 | 24.8947 | 42.5029 | [14 empty] | 0.30106 |  | 162.7938 |  |  |  | 527.1463 |  | 319.5363 |  | 296.9679 |  | 300.7214 |  | 310.0476
03/14 20:00:00 | 21.8196 | 22.5771 | 22.4423 | 22.1847 | 22.0867 | 22.6637 | 21.3503 | 29.7631 | 18.9176 | 23.5261 | 31.1322 | 37.0984 | 23.8454 | 5.6855 | [14 empty] | 0.22024 |  | 579.7313 |  |  |  | 175.0889 |  | 318.2865 |  | 647.5354 |  | 986.7719 |  | 329.7829
03/14 21:00:00 | 21.3992 | 22.0284 | 22.0242 | 21.6224 | 21.5047 | 22.0208 | 20.2327 | 24.4024 | 14.1267 | 17.8202 | 25.2056 | 27.0242 | 18.5028 | 3.8692 | [14 empty] | 1.3608 |  | 421.6097 |  |  |  | 105.215 |  | 194.6294 |  | 455.2392 |  | 536.1523 |  | 214.1418
03/14 22:00:00 | 21.1236 | 21.5222 | 21.6489 | 21.325 | 21.3112 | 21.5234 | 19.2013 | 21.9341 | 13.757 | 17.1436 | 21.0177 | 21.8506 | 17.6416 | 32.6998 | [14 empty] | 3.6953 |  | 115.8994 |  |  |  | 358.828 |  | 241.9937 |  | 136.4719 |  | 117.7048 |  | 226.7488
03/14 23:00:00 | 20.7331 | 21.0283 | 21.2287 | 20.8993 | 20.8941 | 20.9965 | 18.5907 | 20.5753 | 13.2096 | 16.1501 | 20.0884 | 20.9983 | 16.4511 | 23.743 | [14 empty] | 4.59 |  | 10.0347 |  |  |  | 110.9527 |  | 57.6532 |  | 13.3561 |  | 7.5338 |  | 53.1724
03/14 24:00:00 | 20.3565 | 20.6488 | 20.8392 | 20.4583 | 20.336 | 20.4267 | 18.1656 | 20.6781 | 12.9818 | 16.0692 | 20.2818 | 21.1837 | 16.7322 | 26.1789 | [14 empty] | 4.8001 |  | 30.2589 |  |  |  | 174.1629 |  | 102.2055 |  | 34.7761 |  | 24.9525 |  | 89.2409
03/15 01:00:00 | 20.042 | 20.2747 | 20.5176 | 20.0526 | 19.8276 | 20.0164 | 17.8724 | 18.6048 | 12.1723 | 14.6333 | 18.1778 | 19.1366 | 14.8225 | 27.1649 | [14 empty] | 4.7072 |  | 73.2754 |  |  |  | 224.776 |  | 157.0413 |  | 80.7679 |  | 64.4535 |  | 152.3344
03/15 02:00:00 | 20.0513 | 20.1512 | 20.54 | 20.0351 | 19.8409 | 19.9908 | 17.5655 | 18.8916 | 11.8557 | 14.7035 | 18.4397 | 19.3098 | 15.2671 | 28.2048 | [14 empty] | 6.1791 |  | 86.7365 |  |  |  | 267.2924 |  | 182.285 |  | 95.358 |  | 79.1213 |  | 167.3837
03/15 03:00:00 | 19.7281 | 19.7046 | 20.142 | 19.6016 | 19.4473 | 19.5467 | 17.3388 | 18.6133 | 12.0272 | 14.6914 | 18.2854 | 19.0918 | 15.2535 | 30.3378 | [14 empty] | 5.709 |  | 137.4634 |  |  |  | 335.2767 |  | 244.8083 |  | 145.2594 |  | 126.4723 |  | 227.5344
03/15 04:00:00 | 19.2611 | 19.2086 | 19.6639 | 19.0901 | 18.9084 | 19.0003 | 17.1309 | 18.3292 | 11.8015 | 14.4742 | 18.0525 | 18.8841 | 15.1806 | 31.271 | [14 empty] | 4.5379 |  | 167.4903 |  |  |  | 379.0586 |  | 282.1301 |  | 174.7281 |  | 153.4351 |  | 258.9007
03/15 05:00:00 | 18.9206 | 18.8817 | 19.3359 | 18.7575 | 18.5425 | 18.6503 | 16.9742 | 17.2627 | 11.548 | 13.792 | 17.0181 | 17.8128 | 14.3018 | 32.236 | [14 empty] | 3.7884 |  | 224.1997 |  |  |  | 427.9922 |  | 340.1795 |  | 231.5816 |  | 208.0264 |  | 321.6336
03/15 06:00:00 | 18.6263 | 18.6157 | 19.0519 | 18.4586 | 18.2473 | 18.3673 | 16.8312 | 17.2721 | 11.3223 | 13.6827 | 17.0022 | 36.2699 | 34.1411 | 32.6129 | [14 empty] | 3.2224 |  | 235.3395 |  |  |  | 453.2859 |  | 358.3501 |  | 243.6932 |  | 13.374 |  | 2.3354
03/15 07:00:00 | 18.3284 | 18.3338 | 18.7594 | 18.1431 | 18.0821 | 18.2244 | 17.3573 | 31.738 | 28.9422 | 13.4441 | 34.7245 | 48.2122 | 47.4712 | 91.3085 | [14 empty] | 0.94308 |  | 3548.6441 |  |  |  | 3889.5538 |  | 6062.8571 |  | 3201.7421 |  | 1857.2898 |  | 1921.7061
03/15 08:00:00 | 18.1876 | 18.1849 | 18.4732 | 17.9846 | 18.2585 | 18.4557 | 18.6053 | 54.3743 | 56.8548 | 36.7056 | 63.612 | 66.2611 | 64.6679 | 65.9752 | [14 empty] | 0.17445 |  | 134.58 |  |  |  | 83.1811 |  | 856.7092 |  | 5.5847 |  | 0.081738 |  | 1.7088
03/15 09:00:00 | 18.6867 | 18.9961 | 18.4617 | 18.8178 | 19.8798 | 19.9812 | 19.5104 | 54.7304 | 53.2479 | 53.3981 | 60.4916 | 60.7097 | 59.9489 | 65.1286 | [14 empty] | 0.67852 |  | 108.1229 |  |  |  | 141.1515 |  | 137.605 |  | 21.502 |  | 19.5268 |  | 26.8295
03/15 10:00:00 | 19.6194 | 20.7453 | 19.2464 | 20.4867 | 21.4954 | 21.6824 | 20.3381 | 54.5811 | 49.8837 | 53.5931 | 58.5315 | 54.7163 | 53.6546 | 65.4437 | [14 empty] | 0.51653 |  | 117.9974 |  |  |  | 242.1158 |  | 140.4369 |  | 47.7786 |  | 115.0776 |  | 138.9837
03/15 11:00:00 | 20.407 | 22.5378 | 20.8061 | 21.9387 | 22.4341 | 22.7612 | 21.1081 | 55.1914 | 42.2704 | 52.9754 | 53.9272 | 48.873 | 48.2354 | 62.471 | [14 empty] | 0.49152 |  | 52.9925 |  |  |  | 408.0664 |  | 90.1673 |  | 72.9963 |  | 184.9069 |  | 202.6538
03/15 12:00:00 | 21.0696 | 23.5495 | 22.1533 | 22.8679 | 22.9478 | 23.3286 | 21.7384 | 55.2259 | 38.6579 | 48.8485 | 48.6744 | 44.7698 | 44.4538 | 42.8521 | [14 empty] | 0.44733 |  | 153.1099 |  |  |  | 17.5918 |  | 35.9562 |  | 33.8993 |  | 3.6774 |  | 2.5654
03/15 13:00:00 | 21.5967 | 23.9409 | 22.909 | 23.2505 | 23.1593 | 23.5718 | 21.6331 | 50.4371 | 35.3601 | 43.6072 | 43.8871 | 41.2094 | 40.6169 | 44.521 | [14 empty] | 0.0013299 |  | 35.0012 |  |  |  | 83.9205 |  | 0.83501 |  | 0.40174 |  | 10.9661 |  | 15.2419
03/15 14:00:00 | 22.1529 | 24.2795 | 23.348 | 23.5053 | 23.353 | 23.8337 | 21.7863 | 48.0372 | 32.699 | 40.2196 | 41.4276 | 38.7092 | 38.0585 | 37.1239 | [14 empty] | 0.13443 |  | 119.099 |  |  |  | 19.5802 |  | 9.5831 |  | 18.5222 |  | 2.5131 |  | 0.87346
03/15 15:00:00 | 22.628 | 24.6077 | 23.6847 | 23.7221 | 23.5472 | 24.1198 | 21.6863 | 43.7853 | 30.5091 | 37.0959 | 37.582 | 35.0229 | 34.5719 | 34.4121 | [14 empty] | 0.8868 |  | 87.8562 |  |  |  | 15.2331 |  | 7.203 |  | 10.0483 |  | 0.37311 |  | 0.025542
03/15 16:00:00 | 22.9369 | 24.8226 | 23.9451 | 23.8835 | 23.7101 | 24.3025 | 21.6133 | 41.149 | 28.7301 | 34.9097 | 35.4483 | 33.1355 | 32.7746 | 39.9432 | [14 empty] | 1.7519 |  | 1.4541 |  |  |  | 125.7337 |  | 25.3363 |  | 20.2037 |  | 46.3451 |  | 51.3881
03/15 17:00:00 | 23.0477 | 24.9438 | 24.077 | 23.9513 | 23.7799 | 24.3875 | 21.6449 | 37.6915 | 26.9143 | 32.2005 | 32.2328 | 30.144 | 29.7721 | 36.0654 | [14 empty] | 1.9676 |  | 2.6443 |  |  |  | 83.7423 |  | 14.9368 |  | 14.6884 |  | 35.0625 |  | 39.6058
03/15 18:00:00 | 23.0535 | 24.9814 | 24.1046 | 23.923 | 23.7551 | 24.3836 | 21.6124 | 34.0097 | 25.0494 | 29.3537 | 28.6457 | 26.7797 | 26.3837 | 42.0342 | [14 empty] | 2.0769 |  | 64.3919 |  |  |  | 288.4809 |  | 160.7931 |  | 179.2514 |  | 232.698 |  | 244.9364
03/15 19:00:00 | 22.97 | 24.9305 | 24.0359 | 23.7719 | 23.6147 | 24.2628 | 21.6521 | 33.0734 | 24.5088 | 28.5348 | 27.9896 | 26.2689 | 25.9512 | 54.8399 | [14 empty] | 1.7369 |  | 473.7793 |  |  |  | 919.9724 |  | 691.9564 |  | 720.9383 |  | 816.3015 |  | 834.5576
03/15 20:00:00 | 22.6705 | 24.5709 | 23.6957 | 23.2933 | 23.1359 | 23.7523 | 21.3883 | 31.6494 | 23.7695 | 27.5881 | 27.0389 | 25.4394 | 25.2108 | 5.0865 | [14 empty] | 1.6439 |  | 705.5887 |  |  |  | 349.0554 |  | 506.3227 |  | 481.9111 |  | 414.241 |  | 404.9888
03/15 21:00:00 | 22.3568 | 24.0904 | 23.3042 | 22.7527 | 22.5827 | 23.1844 | 20.2224 | 25.0693 | 17.7497 | 21.0272 | 21.1537 | 19.9178 | 19.8503 | 3.844 | [14 empty] | 4.5557 |  | 450.5122 |  |  |  | 193.3685 |  | 295.262 |  | 299.6247 |  | 258.3673 |  | 256.2008
03/15 22:00:00 | 22.0519 | 23.596 | 22.9898 | 22.2347 | 22.0209 | 22.6638 | 19.2127 | 23.6017 | 17.2164 | 20.0595 | 19.9225 | 18.8187 | 18.7162 | 27.5732 | [14 empty] | 8.0608 |  | 15.7729 |  |  |  | 107.2624 |  | 56.4559 |  | 58.5334 |  | 76.6416 |  | 78.4469
03/15 23:00:00 | 21.7122 | 23.1034 | 22.6596 | 21.737 | 21.4032 | 22.1548 | 18.7215 | 23.323 | 16.8528 | 19.6755 | 19.9274 | 18.8683 | 18.7666 | 22.6586 | [14 empty] | 8.944 |  | 0.44147 |  |  |  | 33.7076 |  | 8.8991 |  | 7.4596 |  | 14.3661 |  | 15.1477
03/15 24:00:00 | 21.3765 | 22.6049 | 22.3321 | 21.237 | 20.8164 | 21.6394 | 18.361 | 22.4844 | 16.4618 | 19.0589 | 19.32 | 18.3393 | 18.215 | 24.8697 | [14 empty] | 9.0932 |  | 5.6896 |  |  |  | 70.6926 |  | 33.7657 |  | 30.7993 |  | 42.6463 |  | 44.2855
03/16 01:00:00 | 21.1115 | 22.2296 | 22.0644 | 20.8704 | 20.3922 | 21.189 | 18.1327 | 21.9932 | 16.1142 | 18.6985 | 18.9167 | 18.0262 | 17.9089 | 26.1021 | [14 empty] | 8.8733 |  | 16.8833 |  |  |  | 99.7576 |  | 54.8135 |  | 51.6302 |  | 65.2205 |  | 67.1291
03/16 02:00:00 | 20.691 | 21.7324 | 21.633 | 20.3424 | 19.8287 | 20.624 | 17.9558 | 20.3473 | 15.4963 | 17.5592 | 17.5994 | 16.7819 | 16.6536 | 25.7047 | [14 empty] | 7.4815 |  | 28.7018 |  |  |  | 104.2127 |  | 66.3506 |  | 65.6963 |  | 79.6177 |  | 81.9236
03/16 03:00:00 | 20.4077 | 21.4044 | 21.348 | 20.0149 | 19.5268 | 20.3231 | 17.7495 | 16.9624 | 14.931 | 17.0436 | 17.2733 | 16.4796 | 16.3658 | 27.4124 | [14 empty] | 7.0657 |  | 109.202 |  |  |  | 155.7841 |  | 107.5114 |  | 102.8013 |  | 119.526 |  | 122.0262
03/16 04:00:00 | 20.2119 | 21.1957 | 21.1344 | 19.801 | 19.3174 | 20.1155 | 17.6138 | 15.9662 | 14.3375 | 13.6556 | 16.1566 | 15.4228 | 15.3074 | 27.7708 | [14 empty] | 6.7503 |  | 139.3478 |  |  |  | 180.453 |  | 199.2369 |  | 134.8892 |  | 152.4716 |  | 155.3361
03/16 05:00:00 | 20.0693 | 20.9795 | 20.9506 | 19.5753 | 19.0899 | 19.8909 | 17.5714 | 16.1277 | 13.935 | 13.7883 | 16.0596 | 15.3556 | 15.2324 | 27.6194 | [14 empty] | 6.2391 |  | 132.0613 |  |  |  | 187.2636 |  | 191.3015 |  | 133.6309 |  | 150.4015 |  | 153.4381
03/16 06:00:00 | 19.9135 | 20.7463 | 20.7982 | 19.3249 | 18.8345 | 19.6389 | 17.5278 | 15.6548 | 13.5565 | 13.4827 | 15.5413 | 14.875 | 14.765 | 28.1451 | [14 empty] | 5.6915 |  | 156.0074 |  |  |  | 212.8277 |  | 214.9853 |  | 158.8558 |  | 176.0951 |  | 179.0275
03/16 07:00:00 | 19.7514 | 20.5042 | 20.6395 | 19.0638 | 18.5669 | 19.3759 | 17.9994 | 15.6196 | 13.1866 | 13.3448 | 15.3853 | 14.7287 | 14.6441 | 80.9644 | [14 empty] | 3.0696 |  | 4269.9443 |  |  |  | 4593.8339 |  | 4572.4186 |  | 4300.6202 |  | 4387.1649 |  | 4398.3864
03/16 08:00:00 | 19.5802 | 20.2508 | 20.4691 | 18.7916 | 18.2879 | 19.1036 | 19.3416 | 36.9879 | 37.4699 | 36.341 | 40.9235 | 43.8665 | 41.7936 | 67.2012 | [14 empty] | 0.056933 |  | 912.846 |  |  |  | 883.952 |  | 952.3536 |  | 690.5193 |  | 544.5086 |  | 645.5454
03/16 09:00:00 | 19.6261 | 20.2541 | 20.5174 | 18.8115 | 18.3227 | 19.1375 | 20.4666 | 51.0679 | 53.4086 | 51.2795 | 60.2495 | 63.2205 | 61.1744 | 64.447 | [14 empty] | 0.70645 |  | 179.0022 |  |  |  | 121.848 |  | 173.3833 |  | 17.6196 |  | 1.5045 |  | 10.7104
03/16 10:00:00 | 20.156 | 21.3798 | 21.2095 | 20.0526 | 19.8161 | 20.5165 | 21.4848 | 51.0544 | 41.1156 | 43.8231 | 55.937 | 57.427 | 54.8519 | 53.2507 | [14 empty] | 1.7658 |  | 4.8241 |  |  |  | 147.2619 |  | 88.881 |  | 7.216 |  | 17.4415 |  | 2.5638
03/16 11:00:00 | 21.215 | 23.3951 | 22.8105 | 22.1745 | 22.1452 | 22.729 | 21.9834 | 44.2245 | 33.1409 | 37.046 | 45.5481 | 45.396 | 42.2121 | 19.3863 | [14 empty] | 0.59036 |  | 616.9352 |  |  |  | 189.1871 |  | 311.8632 |  | 684.4377 |  | 676.505 |  | 521.015
03/16 12:00:00 | 22.4015 | 24.6586 | 23.8579 | 23.6915 | 23.5882 | 24.2435 | 21.9673 | 40.7472 | 30.8606 | 34.4022 | 41.1526 | 40.7219 | 38.4754 | 29.4038 | [14 empty] | 0.1885 |  | 128.6732 |  |  |  | 2.1224 |  | 24.9843 |  | 138.0345 |  | 128.0996 |  | 82.2955
03/16 13:00:00 | 22.9372 | 25.0796 | 24.1982 | 24.2077 | 24.1351 | 24.7036 | 21.9009 | 37.8328 | 28.671 | 32.102 | 37.9536 | 37.7509 | 35.7349 | 31.0663 | [14 empty] | 1.0739 |  | 45.7856 |  |  |  | 5.7377 |  | 1.0726 |  | 47.434 |  | 44.683 |  | 21.7956
03/16 14:00:00 | 23.2 | 25.3531 | 24.4013 | 24.4214 | 24.3479 | 24.9443 | 21.9177 | 34.2708 | 25.4306 | 28.848 | 33.9435 | 33.6728 | 31.7755 | 28.9921 | [14 empty] | 1.6442 |  | 27.8652 |  |  |  | 12.6841 |  | 0.020759 |  | 24.5164 |  | 21.9095 |  | 7.7472
03/16 15:00:00 | 23.617 | 25.7549 | 24.7921 | 24.7178 | 24.6712 | 25.2916 | 22.1125 | 28.4511 | 21.1542 | 24.1543 | 27.4989 | 27.1889 | 25.4091 | 24.9731 | [14 empty] | 2.2635 |  | 12.0971 |  |  |  | 14.5837 |  | 0.67031 |  | 6.3798 |  | 4.9099 |  | 0.19014
03/16 16:00:00 | 24.081 | 26.2596 | 25.2496 | 25.1575 | 25.1468 | 25.7754 | 22.1203 | 25.2579 | 16.2947 | 20.7874 | 23.7085 | 23.2434 | 21.0619 | 25.8365 | [14 empty] | 3.8444 |  | 0.33472 |  |  |  | 91.0454 |  | 25.4933 |  | 4.5281 |  | 6.724 |  | 22.7965
03/16 17:00:00 | 24.4349 | 26.651 | 25.6017 | 25.5315 | 25.5495 | 26.1923 | 22.1371 | 24.6404 | 16.1325 | 20.1021 | 23.2751 | 23.0408 | 20.8258 | 24.295 | [14 empty] | 5.2802 |  | 0.11933 |  |  |  | 66.6262 |  | 17.5801 |  | 1.0403 |  | 1.573 |  | 12.0356
03/16 18:00:00 | 24.5762 | 26.8175 | 25.7371 | 25.6575 | 25.6879 | 26.3404 | 22.0678 | 24.9812 | 18.5612 | 20.8688 | 24.3873 | 24.3026 | 22.6011 | 26.3395 | [14 empty] | 6.2921 |  | 1.8452 |  |  |  | 60.5032 |  | 29.9291 |  | 3.8111 |  | 4.1492 |  | 13.9758
03/16 19:00:00 | 24.4911 | 26.7005 | 25.627 | 25.5156 | 25.5396 | 26.1843 | 21.7926 | 27.1357 | 21.8964 | 22.953 | 27.1803 | 27.3901 | 26.754 | 28.4139 | [14 empty] | 7.282 |  | 1.6339 |  |  |  | 42.4776 |  | 29.8217 |  | 1.5217 |  | 1.0482 |  | 2.7553
03/16 20:00:00 | 24.0359 | 26.1379 | 25.1703 | 25.0074 | 25.0285 | 25.6367 | 21.2978 | 26.6792 | 21.4692 | 22.7369 | 26.4494 | 26.3811 | 25.8923 | 4.817 | [14 empty] | 7.4969 |  | 477.9557 |  |  |  | 277.2954 |  | 321.1204 |  | 467.961 |  | 465.0072 |  | 444.1648
03/16 21:00:00 | 23.6058 | 25.6549 | 24.7706 | 24.5281 | 24.5559 | 25.1679 | 20.4918 | 21.0206 | 16.0355 | 17.3572 | 20.3892 | 20.2061 | 19.8797 | 3.5122 | [14 empty] | 9.6968 |  | 306.5449 |  |  |  | 156.8348 |  | 191.6854 |  | 284.8344 |  | 278.6868 |  | 267.8961
03/16 22:00:00 | 23.337 | 25.3345 | 24.4591 | 24.1782 | 24.122 | 24.7678 | 19.6874 | 20.5095 | 15.6515 | 16.9223 | 19.847 | 19.7521 | 19.3764 | 12.1761 | [14 empty] | 13.3199 |  | 69.4445 |  |  |  | 12.0778 |  | 22.5264 |  | 58.8416 |  | 57.3946 |  | 51.8435
03/16 23:00:00 | 23.0353 | 24.952 | 24.1297 | 23.7654 | 23.5839 | 24.2957 | 19.2732 | 20.5336 | 15.4582 | 16.8364 | 19.9412 | 19.8668 | 19.5496 | 18.0677 | [14 empty] | 14.1531 |  | 6.0804 |  |  |  | 6.8098 |  | 1.5162 |  | 3.5101 |  | 3.2366 |  | 2.1961
03/16 24:00:00 | 22.6532 | 24.474 | 23.7775 | 23.2514 | 23.0162 | 23.7975 | 19.0178 | 19.0186 | 15.0117 | 15.9601 | 18.5963 | 18.559 | 18.2103 | 19.4323 | [14 empty] | 13.2158 |  | 0.17109 |  |  |  | 19.5417 |  | 12.0563 |  | 0.69877 |  | 0.76261 |  | 1.4931
03/17 01:00:00 | 22.3772 | 24.1048 | 23.514 | 22.8652 | 22.5763 | 23.3438 | 18.853 | 18.7377 | 14.668 | 15.6942 | 18.2542 | 18.2184 | 17.9175 | 20.2131 | [14 empty] | 12.4198 |  | 2.1767 |  |  |  | 30.7482 |  | 20.4202 |  | 3.8371 |  | 3.9787 |  | 5.2698
03/17 02:00:00 | 21.9832 | 23.6301 | 23.0619 | 22.3481 | 21.996 | 22.8005 | 18.6999 | 18.3204 | 14.4083 | 15.3577 | 17.9683 | 17.9875 | 17.6481 | 21.6378 | [14 empty] | 10.78 |  | 11.0051 |  |  |  | 52.2656 |  | 39.439 |  | 13.4654 |  | 13.3247 |  | 15.9177
03/17 03:00:00 | 21.6585 | 23.2136 | 22.7062 | 21.9594 | 21.547 | 22.4366 | 18.484 | 18.0736 | 14.1073 | 15.1004 | 17.7472 | 17.7549 | 17.4364 | 21.706 | [14 empty] | 10.0775 |  | 13.1943 |  |  |  | 57.7397 |  | 43.6333 |  | 15.6723 |  | 15.611 |  | 18.2296
03/17 04:00:00 | 21.3735 | 22.8384 | 22.4384 | 21.6105 | 21.1669 | 22.0902 | 18.298 | 17.3609 | 13.7936 | 14.647 | 17.0866 | 17.0987 | 16.8041 | 23.5754 | [14 empty] | 9.4591 |  | 38.6192 |  |  |  | 95.6842 |  | 79.7154 |  | 42.1039 |  | 41.9469 |  | 45.8503
03/17 05:00:00 | 21.0564 | 22.4323 | 22.1322 | 21.1528 | 20.7318 | 21.6301 | 18.1439 | 17.0419 | 13.4917 | 14.3271 | 16.7714 | 16.81 | 16.5093 | 23.4769 | [14 empty] | 8.4825 |  | 41.4086 |  |  |  | 99.7045 |  | 83.7181 |  | 44.9627 |  | 44.4477 |  | 48.5477
03/17 06:00:00 | 20.7275 | 22.0948 | 21.8067 | 20.7789 | 20.2789 | 21.2536 | 18.0194 | 16.5075 | 13.1353 | 13.9592 | 16.2936 | 16.3343 | 16.0471 | 25.1004 | [14 empty] | 7.3337 |  | 73.8369 |  |  |  | 143.1618 |  | 124.1252 |  | 77.5595 |  | 76.8431 |  | 81.9623
03/17 07:00:00 | 20.3924 | 21.7768 | 21.4732 | 20.4271 | 19.9148 | 20.8987 | 18.517 | 15.5631 | 12.7096 | 13.338 | 15.3673 | 15.4362 | 15.1361 | 82.8251 | [14 empty] | 3.5171 |  | 4524.1763 |  |  |  | 4916.1831 |  | 4828.4606 |  | 4550.5615 |  | 4541.2702 |  | 4581.8106
03/17 08:00:00 | 20.1058 | 21.493 | 21.1877 | 20.1182 | 19.6171 | 20.5867 | 20.1016 | 35.298 | 16.5039 | 34.2715 | 40.5463 | 43.8996 | 41.607 | 64.194 | [14 empty] | 1.7606e-05 |  | 834.9776 |  |  |  | 2274.3438 |  | 895.3537 |  | 559.2132 |  | 411.8615 |  | 510.1717
03/17 09:00:00 | 20.2448 | 21.4843 | 21.3516 | 20.2641 | 19.7929 | 20.748 | 21.6466 | 49.8063 | 33.3262 | 41.6358 | 58.1435 | 60.9541 | 58.0586 | 37.515 | [14 empty] | 1.965 |  | 151.0754 |  |  |  | 17.5458 |  | 16.9809 |  | 425.5356 |  | 549.3943 |  | 422.0401
03/17 10:00:00 | 21.3418 | 22.0901 | 22.6325 | 22.1304 | 21.9668 | 22.7719 | 22.1962 | 41.6698 | 36.0066 | 31.1378 | 42.6729 | 43.3471 | 38.2837 | 8.8605 | [14 empty] | 0.72997 |  | 1076.4483 |  |  |  | 736.9092 |  | 496.2789 |  | 1143.2752 |  | 1189.3238 |  | 865.723
03/17 11:00:00 | 22.9769 | 24.0091 | 24.2062 | 24.5056 | 24.5922 | 25.2247 | 22.3047 | 35.2728 | 24.6561 | 27.104 | 34.934 | 34.561 | 30.9876 | 20.6535 | [14 empty] | 0.45181 |  | 213.7247 |  |  |  | 16.0214 |  | 41.6097 |  | 203.9345 |  | 193.4186 |  | 106.7946
03/17 12:00:00 | 24.3378 | 25.8668 | 25.285 | 25.637 | 25.5497 | 26.1103 | 22.4449 | 33.3197 | 21.9336 | 25.6401 | 33.196 | 33.0028 | 30.3301 | 3.5717 | [14 empty] | 3.583 |  | 884.9411 |  |  |  | 337.1571 |  | 487.0137 |  | 877.5987 |  | 866.1858 |  | 716.0086
03/17 13:00:00 | 24.6725 | 26.3305 | 25.5094 | 25.7619 | 25.6959 | 26.26 | 22.3688 | 31.572 | 21.0227 | 24.5019 | 31.3927 | 31.2899 | 28.7733 | 19.7577 | [14 empty] | 5.307 |  | 139.5767 |  |  |  | 1.6001 |  | 22.507 |  | 135.3731 |  | 132.991 |  | 81.2808
03/17 14:00:00 | 24.7201 | 26.4 | 25.5813 | 25.8067 | 25.7567 | 26.3282 | 22.3162 | 30.1273 | 20.2796 | 23.5132 | 29.9525 | 29.8537 | 27.6075 | 16.2142 | [14 empty] | 5.779 |  | 193.5726 |  |  |  | 16.5275 |  | 53.2746 |  | 188.7398 |  | 186.0366 |  | 129.8064
03/17 15:00:00 | 24.9322 | 26.6558 | 25.8186 | 26.0262 | 25.9905 | 26.5688 | 22.0697 | 28.7053 | 20.0381 | 22.5237 | 28.877 | 28.8825 | 26.931 | 21.9728 | [14 empty] | 8.1937 |  | 45.3269 |  |  |  | 3.7428 |  | 0.30353 |  | 47.6678 |  | 47.7448 |  | 24.5839
03/17 16:00:00 | 24.9866 | 26.704 | 25.875 | 26.0658 | 26.0359 | 26.5515 | 21.8592 | 27.2769 | 19.2985 | 21.5437 | 27.1298 | 27.1172 | 25.7697 | 26.8238 | [14 empty] | 9.7803 |  | 0.20527 |  |  |  | 56.6307 |  | 27.8796 |  | 0.093652 |  | 0.086099 |  | 1.1111
03/17 17:00:00 | 24.7723 | 26.4734 | 25.6842 | 25.7562 | 25.735 | 26.2828 | 21.6431 | 26.4066 | 18.699 | 20.9687 | 26.1329 | 26.0802 | 24.7016 | 40.2483 | [14 empty] | 9.7916 |  | 191.5926 |  |  |  | 464.372 |  | 371.7018 |  | 199.2428 |  | 200.7342 |  | 241.6996
03/17 18:00:00 | 24.3725 | 26.0258 | 25.2975 | 25.2394 | 25.2336 | 25.8045 | 21.81 | 25.3694 | 18.2116 | 20.2661 | 25.0514 | 24.9398 | 23.6958 | 29.4513 | [14 empty] | 6.5667 |  | 16.6622 |  |  |  | 126.3314 |  | 84.3681 |  | 19.3593 |  | 20.3542 |  | 33.1262
03/17 19:00:00 | 23.7752 | 25.4007 | 24.664 | 24.6182 | 24.5073 | 25.1622 | 21.7157 | 24.018 | 17.6066 | 19.3767 | 23.6139 | 23.5479 | 22.39 | 31.9684 | [14 empty] | 4.2414 |  | 63.2092 |  |  |  | 206.2617 |  | 158.5508 |  | 69.7976 |  | 70.9063 |  | 91.7465
03/17 20:00:00 | 23.1786 | 24.78 | 24.0476 | 24.0031 | 23.7936 | 24.5302 | 21.4794 | 23.37 | 17.0737 | 18.7416 | 22.9555 | 22.9209 | 21.7923 | 4.7781 | [14 empty] | 2.8872 |  | 345.6606 |  |  |  | 151.1813 |  | 194.9795 |  | 330.4169 |  | 329.1603 |  | 289.4839
03/17 21:00:00 | 22.7699 | 24.2221 | 23.6244 | 23.4595 | 23.2785 | 23.9696 | 20.8773 | 18.2043 | 12.6931 | 14.2392 | 17.6614 | 17.5804 | 16.8252 | 3.4653 | [14 empty] | 3.5818 |  | 217.2383 |  |  |  | 85.1529 |  | 116.0775 |  | 201.5313 |  | 199.2362 |  | 178.4864
03/17 22:00:00 | 22.4275 | 23.8143 | 23.2727 | 22.9736 | 22.8185 | 23.4646 | 20.1591 | 17.7026 | 12.4091 | 13.8768 | 17.1749 | 17.0626 | 16.3854 | 3.221 | [14 empty] | 5.1456 |  | 209.7173 |  |  |  | 84.4209 |  | 113.5457 |  | 194.7103 |  | 191.5911 |  | 173.3011
03/17 23:00:00 | 22.066 | 23.4636 | 22.9023 | 22.5185 | 22.3315 | 22.9942 | 19.6162 | 16.0823 | 11.8776 | 12.9169 | 15.6971 | 15.6769 | 14.982 | 17.2519 | [14 empty] | 6.0013 |  | 1.368 |  |  |  | 28.8829 |  | 18.7922 |  | 2.4174 |  | 2.4806 |  | 5.1525
03/17 24:00:00 | 21.7376 | 23.1285 | 22.5622 | 22.1014 | 21.8814 | 22.5636 | 19.4699 | 15.0716 | 11.3676 | 12.237 | 14.7116 | 14.7158 | 14.0501 | 16.815 | [14 empty] | 5.1427 |  | 3.0394 |  |  |  | 29.674 |  | 20.9577 |  | 4.4243 |  | 4.4068 |  | 7.6447
03/18 01:00:00 | 21.4883 | 22.8323 | 22.3082 | 21.8159 | 21.5146 | 22.2695 | 19.3156 | 15.078 | 11.1452 | 12.1845 | 14.6952 | 14.6587 | 14.044 | 16.2241 | [14 empty] | 4.7203 |  | 1.3137 |  |  |  | 25.7959 |  | 16.3192 |  | 2.3377 |  | 2.4505 |  | 4.7529
03/18 02:00:00 | 21.0751 | 22.3547 | 21.8831 | 21.3661 | 20.9718 | 21.8131 | 19.221 | 14.2673 | 10.941 | 11.6255 | 13.9728 | 14.0149 | 13.3654 | 17.1449 | [14 empty] | 3.4376 |  | 8.2806 |  |  |  | 38.488 |  | 30.4632 |  | 10.0624 |  | 9.7966 |  | 14.2843
03/18 03:00:00 | 20.7567 | 21.9755 | 21.5476 | 21.0151 | 20.5822 | 21.456 | 19.1148 | 11.6099 | 10.5374 | 11.2667 | 13.5296 | 13.5553 | 12.9287 | 17.3338 | [14 empty] | 2.6958 |  | 32.7631 |  |  |  | 46.191 |  | 36.8097 |  | 14.4715 |  | 14.2769 |  | 19.4049
03/18 04:00:00 | 20.5404 | 21.6661 | 21.291 | 20.7319 | 20.315 | 21.1679 | 19.0535 | 13.7993 | 10.2938 | 9.3965 | 13.235 | 13.2456 | 12.6554 | 17.8729 | [14 empty] | 2.2109 |  | 16.5949 |  |  |  | 57.4429 |  | 71.8497 |  | 21.5106 |  | 21.4124 |  | 27.2226
03/18 05:00:00 | 20.3509 | 21.3684 | 21.086 | 20.4484 | 20.0382 | 20.8786 | 18.9863 | 11.0839 | 10.0448 | 9.3291 | 12.774 | 12.7816 | 12.2148 | 17.4678 | [14 empty] | 1.862 |  | 40.7545 |  |  |  | 55.1009 |  | 66.2389 |  | 22.0313 |  | 21.9607 |  | 27.5943
03/18 06:00:00 | 20.1369 | 21.0802 | 20.9347 | 20.1687 | 19.7566 | 20.5862 | 18.9269 | 10.5986 | 8.4629 | 8.9863 | 12.0989 | 12.1135 | 11.5962 | 18.6202 | [14 empty] | 1.4641 |  | 64.3465 |  |  |  | 103.1709 |  | 92.8128 |  | 42.5267 |  | 42.3372 |  | 49.3369
03/18 07:00:00 | 19.9829 | 20.8615 | 20.784 | 19.8888 | 19.4717 | 20.3095 | 18.899 | 10.4656 | 8.417 | 8.8168 | 10.5736 | 11.8246 | 10.2559 | 17.6513 | [14 empty] | 1.1748 |  | 51.6347 |  |  |  | 85.2727 |  | 78.0493 |  | 50.0933 |  | 33.9503 |  | 54.6924
03/18 08:00:00 | 19.827 | 20.7044 | 20.6285 | 19.672 | 19.1953 | 20.0961 | 19.4461 | 10.2388 | 8.2353 | 8.6081 | 10.4494 | 10.469 | 10.1227 | 84.3235 | [14 empty] | 0.14507 |  | 5488.5401 |  |  |  | 5789.4058 |  | 5732.8161 |  | 5457.371 |  | 5454.4779 |  | 5505.7495
03/18 09:00:00 | 19.6749 | 20.5521 | 20.4772 | 19.5183 | 18.9884 | 19.9458 | 20.5895 | 13.0344 | 10.8054 | 11.0171 | 13.0949 | 13.4731 | 12.6506 | 14.5631 | [14 empty] | 0.83652 |  | 2.337 |  |  |  | 14.1202 |  | 12.5736 |  | 2.1555 |  | 1.188 |  | 3.6574
03/18 10:00:00 | 19.5282 | 20.4033 | 20.3326 | 19.3688 | 18.8445 | 19.7977 | 20.6675 | 33.2395 | 12.7532 | 10.184 | 39.6976 | 46.862 | 16.345 | 22.7996 | [14 empty] | 1.2982 |  | 108.9912 |  |  |  | 100.9306 |  | 159.153 |  | 285.5432 |  | 579.0015 |  | 41.6611
03/18 11:00:00 | 19.5268 | 20.2519 | 20.215 | 19.4575 | 18.9762 | 19.6538 | 20.7932 | 49.3631 | 25.1236 | 16.8105 | 57.8976 | 60.7099 | 33.4759 | 6.5953 | [14 empty] | 1.6037 |  | 1829.0832 |  |  |  | 343.2954 |  | 104.3489 |  | 2631.9225 |  | 2928.3883 |  | 722.5646
03/18 12:00:00 | 20.0383 | 20.1973 | 20.1477 | 20.4586 | 20.3665 | 19.7296 | 20.6892 | 42.3312 | 34.7656 | 20.7655 | 43.9252 | 43.9691 | 40.6691 | 19.2408 | [14 empty] | 0.42365 |  | 533.1641 |  |  |  | 241.0189 |  | 2.3245 |  | 609.3165 |  | 611.4886 |  | 459.1696
03/18 13:00:00 | 20.7233 | 20.5001 | 20.1605 | 22.0239 | 22.1482 | 20.2995 | 20.6934 | 36.7349 | 34.3213 | 26.2962 | 37.0421 | 36.6332 | 39.4989 | 14.3215 | [14 empty] | 0.00089178 |  | 502.3597 |  |  |  | 399.9903 |  | 143.3931 |  | 516.2231 |  | 497.8125 |  | 633.8989
03/18 14:00:00 | 21.0477 | 21.1208 | 20.2585 | 22.6633 | 22.5984 | 21.1301 | 20.7043 | 33.8769 | 27.2342 | 34.1256 | 34.0246 | 33.8671 | 31.7089 | 3.7205 | [14 empty] | 0.11796 |  | 909.4096 |  |  |  | 552.8974 |  | 924.4739 |  | 918.3378 |  | 908.8219 |  | 783.3535
03/18 15:00:00 | 21.337 | 21.8895 | 20.6514 | 22.8134 | 22.7286 | 21.8715 | 20.7335 | 31.7554 | 23.8696 | 28.3541 | 31.7888 | 31.7397 | 28.0609 | 3.141 | [14 empty] | 0.36423 |  | 818.7823 |  |  |  | 429.6764 |  | 635.6991 |  | 820.6986 |  | 817.8868 |  | 621.0001
03/18 16:00:00 | 21.5667 | 22.3153 | 21.204 | 22.9117 | 22.8353 | 22.2067 | 20.6903 | 29.1735 | 22.4051 | 25.2135 | 29.1382 | 29.1379 | 26.0366 | 20.2361 | [14 empty] | 0.7681 |  | 79.8773 |  |  |  | 4.7044 |  | 24.7744 |  | 79.2467 |  | 79.2406 |  | 33.645
03/18 17:00:00 | 21.6954 | 22.5286 | 21.5407 | 22.9723 | 22.912 | 22.3599 | 20.6902 | 28.2928 | 21.5449 | 24.5 | 28.0717 | 28.0571 | 25.244 | 13.9027 | [14 empty] | 1.0106 |  | 207.0745 |  |  |  | 58.403 |  | 112.303 |  | 200.7613 |  | 200.3465 |  | 128.6255
03/18 18:00:00 | 21.7055 | 22.5886 | 21.6351 | 22.9127 | 22.8691 | 22.3714 | 20.5507 | 27.5384 | 20.8425 | 23.8717 | 27.1555 | 27.1448 | 24.4979 | 23.1779 | [14 empty] | 1.3335 |  | 19.0144 |  |  |  | 5.4539 |  | 0.4814 |  | 15.8217 |  | 15.7368 |  | 1.7424
03/18 19:00:00 | 21.6182 | 22.488 | 21.6053 | 22.725 | 22.7029 | 22.2306 | 20.4429 | 25.4554 | 19.8958 | 19.3056 | 25.0749 | 25.0205 | 22.6632 | 4.3843 | [14 empty] | 1.3814 |  | 443.9885 |  |  |  | 240.6051 |  | 222.6457 |  | 428.0986 |  | 425.8514 |  | 334.1181
03/18 20:00:00 | 21.4896 | 22.3513 | 21.5176 | 22.4908 | 22.4808 | 22.036 | 20.0316 | 20.8548 | 14.7214 | 17.9096 | 20.0421 | 19.8291 | 18.1735 | 3.3598 | [14 empty] | 2.1257 |  | 306.0743 |  |  |  | 129.0849 |  | 211.6947 |  | 278.2989 |  | 271.2365 |  | 219.4458
03/18 21:00:00 | 21.3231 | 22.1704 | 21.4172 | 22.2152 | 22.1401 | 21.7927 | 19.5385 | 16.4479 | 14.3269 | 16.7201 | 18.8456 | 18.7703 | 17.1136 | 12.1976 | [14 empty] | 3.1849 |  | 18.0651 |  |  |  | 4.534 |  | 20.4532 |  | 44.1961 |  | 43.2007 |  | 24.1669
03/18 22:00:00 | 21.1479 | 21.9101 | 21.2506 | 21.8731 | 21.7336 | 21.4738 | 19.3614 | 15.9979 | 13.8516 | 13.4107 | 18.1109 | 18.032 | 16.4798 | 15.8507 | [14 empty] | 3.1916 |  | 0.021661 |  |  |  | 3.9967 |  | 5.9539 |  | 5.1084 |  | 4.7579 |  | 0.3957
03/18 23:00:00 | 21.0033 | 21.6841 | 21.0873 | 21.5263 | 21.3133 | 21.1488 | 19.2375 | 15.6534 | 13.4237 | 13.3531 | 17.5147 | 17.493 | 15.956 | 16.7916 | [14 empty] | 3.1181 |  | 1.2954 |  |  |  | 11.3423 |  | 11.8232 |  | 0.52292 |  | 0.49199 |  | 0.69813
03/18 24:00:00 | 20.8565 | 21.4764 | 20.9612 | 21.2649 | 20.983 | 20.9027 | 19.1191 | 15.1428 | 12.9468 | 12.9988 | 16.8571 | 16.8336 | 15.3677 | 17.5651 | [14 empty] | 3.0187 |  | 5.8674 |  |  |  | 21.3282 |  | 20.8507 |  | 0.50116 |  | 0.53505 |  | 4.8282
03/19 01:00:00 | 20.7047 | 21.2632 | 20.8291 | 21.0224 | 20.665 | 20.674 | 19.043 | 14.9015 | 12.6026 | 12.7287 | 16.4389 | 16.4219 | 14.9854 | 17.9825 | [14 empty] | 2.7612 |  | 9.4924 |  |  |  | 28.9432 |  | 27.6022 |  | 2.3828 |  | 2.4354 |  | 8.9824
03/19 02:00:00 | 20.5413 | 21.0358 | 20.6826 | 20.7624 | 20.3944 | 20.4258 | 18.9892 | 14.1699 | 10.53 | 12.23 | 15.5821 | 15.5987 | 14.2146 | 17.4903 | [14 empty] | 2.4091 |  | 11.0257 |  |  |  | 48.446 |  | 27.6711 |  | 3.6414 |  | 3.5784 |  | 10.7306
03/19 03:00:00 | 20.3874 | 20.8466 | 20.5429 | 20.5136 | 20.1505 | 20.1894 | 18.9708 | 13.3773 | 12.0788 | 11.687 | 14.6823 | 14.7118 | 13.386 | 17.4861 | [14 empty] | 2.0069 |  | 16.8823 |  |  |  | 29.2383 |  | 33.6296 |  | 7.8611 |  | 7.6965 |  | 16.8105
03/19 04:00:00 | 20.2283 | 20.6838 | 20.3969 | 20.2649 | 19.901 | 19.9454 | 18.9402 | 12.8753 | 9.8245 | 11.2723 | 12.5195 | 14.0208 | 11.5534 | 18.4311 | [14 empty] | 1.6592 |  | 30.8663 |  |  |  | 74.0731 |  | 51.2482 |  | 34.947 |  | 19.4504 |  | 47.3021
03/19 05:00:00 | 20.0718 | 20.4898 | 20.2529 | 20.0662 | 19.6515 | 19.755 | 18.92 | 12.4542 | 9.7107 | 10.9253 | 12.2412 | 13.4726 | 11.2912 | 18.1061 | [14 empty] | 1.3267 |  | 31.9437 |  |  |  | 70.4828 |  | 51.5641 |  | 34.397 |  | 21.4692 |  | 46.4427
03/19 06:00:00 | 19.9149 | 20.3522 | 20.1062 | 19.9158 | 19.3896 | 19.6124 | 18.9081 | 12.2391 | 9.5133 | 10.6878 | 12.0381 | 13.1282 | 11.1151 | 17.6758 | [14 empty] | 1.0137 |  | 29.5568 |  |  |  | 66.6259 |  | 48.8314 |  | 31.7836 |  | 20.6806 |  | 43.042
03/19 07:00:00 | 19.7558 | 20.21 | 19.9476 | 19.7581 | 19.1287 | 19.463 | 18.8924 | 12.0081 | 9.3079 | 10.5074 | 11.7873 | 12.8318 | 10.9202 | 18.5467 | [14 empty] | 0.74545 |  | 42.7531 |  |  |  | 85.3546 |  | 64.6306 |  | 45.6888 |  | 32.6598 |  | 58.1624
03/19 08:00:00 | 19.5954 | 20.0636 | 19.8036 | 19.5845 | 18.8707 | 19.3067 | 19.4514 | 11.2193 | 8.9529 | 9.9099 | 11.0178 | 10.881 | 10.1634 | 77.1931 | [14 empty] | 0.020735 |  | 4352.5399 |  |  |  | 4656.7226 |  | 4527.0189 |  | 4379.1677 |  | 4397.2946 |  | 4492.9796
03/19 09:00:00 | 19.4531 | 19.9435 | 19.6714 | 19.4401 | 18.6874 | 19.1742 | 20.619 | 33.2382 | 12.9232 | 14.0381 | 38.2868 | 41.6719 | 39.2092 | 15.2522 | [14 empty] | 1.3595 |  | 323.4957 |  |  |  | 5.4246 |  | 1.4742 |  | 530.5905 |  | 697.9968 |  | 573.9365
03/19 10:00:00 | 19.4721 | 19.8222 | 19.5598 | 19.4575 | 18.7752 | 19.2282 | 20.7768 | 49.464 | 27.9966 | 36.9615 | 58.4485 | 61.4728 | 59.8311 | 8.0538 | [14 empty] | 1.7024 |  | 1714.8056 |  |  |  | 397.7142 |  | 835.6541 |  | 2539.6322 |  | 2853.5929 |  | 2680.895
03/19 11:00:00 | 20.0579 | 19.7929 | 19.663 | 20.6031 | 20.2199 | 20.5529 | 20.6818 | 42.1604 | 36.5396 | 39.884 | 41.1621 | 44.4583 | 43.9351 | 17.6999 | [14 empty] | 0.38929 |  | 598.3148 |  |  |  | 354.9325 |  | 492.1345 |  | 550.4727 |  | 716.0096 |  | 688.2838
03/19 12:00:00 | 20.806 | 20.4256 | 20.4879 | 22.2947 | 22.1019 | 22.5076 | 20.7396 | 35.9674 | 35.0264 | 35.5628 | 34.5823 | 35.9189 | 35.9639 | 6.4517 | [14 empty] | 0.0044093 |  | 871.1755 |  |  |  | 816.51 |  | 847.4542 |  | 791.327 |  | 868.3171 |  | 870.9691
03/19 13:00:00 | 21.1686 | 21.3668 | 21.166 | 22.7608 | 22.8024 | 23.1142 | 20.6585 | 34.4837 | 28.5217 | 32.2348 | 33.3715 | 34.5491 | 34.286 | 20.7492 | [14 empty] | 0.26017 |  | 188.6344 |  |  |  | 60.4106 |  | 131.9182 |  | 159.321 |  | 190.4367 |  | 183.2429
03/19 14:00:00 | 21.351 | 22.0255 | 21.5029 | 22.8046 | 22.8784 | 23.2024 | 20.6566 | 27.5811 | 25.2986 | 29.667 | 31.5186 | 32.7459 | 32.3997 | 3.9852 | [14 empty] | 0.48224 |  | 556.7657 |  |  |  | 454.2585 |  | 659.5544 |  | 758.0878 |  | 827.1765 |  | 807.3832
03/19 15:00:00 | 21.3996 | 22.283 | 21.7049 | 22.8283 | 22.9154 | 23.2639 | 20.6937 | 31.1685 | 23.794 | 27.6927 | 29.0377 | 30.2079 | 29.848 | 11.9692 | [14 empty] | 0.49829 |  | 368.6152 |  |  |  | 139.826 |  | 247.2284 |  | 291.3355 |  | 332.6521 |  | 319.6536
03/19 16:00:00 | 21.5325 | 22.4641 | 21.9097 | 22.8563 | 22.9656 | 23.3383 | 20.6329 | 24.5987 | 22.4884 | 22.5819 | 27.3028 | 28.3889 | 28.0589 | 18.9413 | [14 empty] | 0.80929 |  | 32.0065 |  |  |  | 12.5823 |  | 13.2541 |  | 69.9146 |  | 89.257 |  | 83.1305
03/19 17:00:00 | 21.57 | 22.5636 | 21.998 | 22.8331 | 22.9661 | 23.3577 | 20.6151 | 28.6353 | 21.5535 | 22.0358 | 26.322 | 27.287 | 26.9432 | 15.0368 | [14 empty] | 0.91196 |  | 184.9216 |  |  |  | 42.4674 |  | 48.9861 |  | 127.3563 |  | 150.0688 |  | 141.7634
03/19 18:00:00 | 21.5691 | 22.5782 | 21.9902 | 22.7527 | 22.9072 | 23.3001 | 20.6044 | 22.5941 | 20.4989 | 20.9867 | 24.596 | 25.3984 | 25.137 | 18.9266 | [14 empty] | 0.9307 |  | 13.4504 |  |  |  | 2.472 |  | 4.244 |  | 32.1416 |  | 41.884 |  | 38.5687
03/19 19:00:00 | 21.5021 | 22.5253 | 21.9561 | 22.6249 | 22.7758 | 23.1619 | 20.4927 | 25.7326 | 19.5374 | 23.5639 | 23.3375 | 24.0701 | 23.8443 | 3.877 | [14 empty] | 1.0189 |  | 477.6686 |  |  |  | 245.2493 |  | 387.5751 |  | 378.7101 |  | 407.7631 |  | 398.6917
03/19 20:00:00 | 21.4364 | 22.4045 | 21.9196 | 22.4324 | 22.5628 | 22.9632 | 20.1313 | 20.5374 | 14.4674 | 17.6407 | 18.4615 | 18.9014 | 18.8663 | 3.3311 | [14 empty] | 1.7035 |  | 296.0563 |  |  |  | 124.0181 |  | 204.765 |  | 228.93 |  | 242.4353 |  | 241.3445
03/19 21:00:00 | 21.3114 | 22.2329 | 21.8307 | 22.1696 | 22.2835 | 22.7201 | 19.7121 | 16.6618 | 14.073 | 14.1602 | 17.8089 | 18.2676 | 18.1581 | 2.9232 | [14 empty] | 2.5579 |  | 188.7495 |  |  |  | 124.319 |  | 126.2717 |  | 221.5864 |  | 235.4527 |  | 232.102
03/19 22:00:00 | 21.1795 | 22.0729 | 21.725 | 21.8911 | 21.9353 | 22.429 | 19.479 | 16.1844 | 13.6238 | 14.0414 | 17.095 | 17.557 | 17.4767 | 18.4165 | [14 empty] | 2.8915 |  | 4.9823 |  |  |  | 22.9704 |  | 19.1423 |  | 1.7464 |  | 0.73878 |  | 0.88334
03/19 23:00:00 | 21.0726 | 21.9165 | 21.6356 | 21.6674 | 21.5944 | 22.1401 | 19.4898 | 15.9659 | 13.2136 | 13.8118 | 16.6944 | 17.1666 | 17.0572 | 13.1257 | [14 empty] | 2.5051 |  | 8.0668 |  |  |  | 0.0077315 |  | 0.47068 |  | 12.736 |  | 16.3286 |  | 15.457
03/19 24:00:00 | 20.9549 | 21.7422 | 21.5344 | 21.4491 | 21.312 | 21.8555 | 19.4981 | 15.2145 | 12.7351 | 13.3017 | 15.8633 | 16.3337 | 16.2086 | 11.2685 | [14 empty] | 2.1223 |  | 15.5709 |  |  |  | 2.1511 |  | 4.1339 |  | 21.1123 |  | 25.6566 |  | 24.4046
03/20 01:00:00 | 20.8295 | 21.5535 | 21.424 | 21.2214 | 21.0799 | 21.6214 | 19.4604 | 16.8765 | 12.2172 | 15.0967 | 14.7315 | 15.2061 | 15.0701 | 13.9081 | [14 empty] | 1.8745 |  | 8.8112 |  |  |  | 2.8591 |  | 1.4127 |  | 0.67799 |  | 1.6846 |  | 1.3502
03/20 02:00:00 | 20.6729 | 21.3447 | 21.2806 | 20.9769 | 20.8101 | 21.3864 | 19.4179 | 13.4424 | 10.185 | 11.7954 | 12.6351 | 14.5281 | 12.9864 | 14.9195 | [14 empty] | 1.5749 |  | 2.182 |  |  |  | 22.4156 |  | 9.76 |  | 5.2187 |  | 0.15319 |  | 3.737
03/20 03:00:00 | 20.5228 | 21.2014 | 21.1449 | 20.8131 | 20.5992 | 21.2265 | 19.3851 | 13.1333 | 10.077 | 11.6758 | 13.8779 | 14.0349 | 14.1787 | 14.6732 | [14 empty] | 1.2944 |  | 2.3712 |  |  |  | 21.1253 |  | 8.9845 |  | 0.63256 |  | 0.40747 |  | 0.2445
03/20 04:00:00 | 20.409 | 21.0928 | 21.0401 | 20.6534 | 20.4096 | 21.0677 | 19.326 | 12.9367 | 9.8711 | 11.4825 | 13.3407 | 13.6611 | 13.6089 | 15.2827 | [14 empty] | 1.1729 |  | 5.5036 |  |  |  | 29.2847 |  | 14.441 |  | 3.7711 |  | 2.6296 |  | 2.8014
03/20 05:00:00 | 20.2882 | 20.9777 | 20.93 | 20.4292 | 20.201 | 20.8349 | 19.2878 | 12.6374 | 9.6401 | 11.2227 | 11.6809 | 13.2799 | 13.2025 | 15.4465 | [14 empty] | 1.0008 |  | 7.8912 |  |  |  | 33.7142 |  | 17.8404 |  | 14.1795 |  | 4.6941 |  | 5.0356
03/20 06:00:00 | 20.1682 | 20.8604 | 20.8182 | 20.245 | 19.9867 | 20.609 | 19.2743 | 11.7623 | 9.2955 | 10.6397 | 10.9822 | 11.2638 | 11.1582 | 15.377 | [14 empty] | 0.79909 |  | 13.0658 |  |  |  | 36.9843 |  | 22.4423 |  | 19.3144 |  | 16.918 |  | 17.7979
03/20 07:00:00 | 20.0476 | 20.7423 | 20.7061 | 20.1144 | 19.8074 | 20.4337 | 19.8247 | 11.5247 | 9.0211 | 10.3297 | 10.7669 | 11.1144 | 11.0054 | 83.835 | [14 empty] | 0.04965 |  | 5228.7831 |  |  |  | 5597.1282 |  | 5403.0347 |  | 5338.9526 |  | 5288.2855 |  | 5304.1524
03/20 08:00:00 | 19.9391 | 20.6356 | 20.5949 | 19.9935 | 19.6901 | 20.3188 | 21.4864 | 36.4383 | 34.8619 | 36.805 | 42.1013 | 45.5469 | 43.4592 | 43.6671 | [14 empty] | 2.3941 |  | 52.2564 |  |  |  | 77.5313 |  | 47.0887 |  | 2.4518 |  | 3.5337 |  | 0.043223
03/20 09:00:00 | 20.2062 | 20.8412 | 20.8998 | 20.2616 | 19.9962 | 20.6211 | 22.3309 | 47.6023 | 50.9206 | 48.5418 | 55.8494 | 58.4289 | 56.1815 | 7.3916 | [14 empty] | 4.5145 |  | 1616.9055 |  |  |  | 1894.7793 |  | 1693.3404 |  | 2348.1581 |  | 2604.8101 |  | 2380.4589
03/20 10:00:00 | 21.5357 | 22.8344 | 22.3585 | 22.3623 | 22.4166 | 22.9537 | 22.542 | 37.2045 | 30.4273 | 34.6137 | 36.9106 | 37.3656 | 36.0268 | 3.3743 | [14 empty] | 1.0125 |  | 1144.4815 |  |  |  | 731.8666 |  | 975.9009 |  | 1124.684 |  | 1155.4071 |  | 1066.1823
03/20 11:00:00 | 23.3329 | 25.4966 | 24.7804 | 24.8511 | 25.0274 | 25.5105 | 22.6556 | 33.8214 | 24.7918 | 31.1877 | 32.9682 | 32.2479 | 31.3723 | 3.1399 | [14 empty] | 0.45882 |  | 941.3534 |  |  |  | 468.8043 |  | 786.6764 |  | 889.7273 |  | 847.2719 |  | 797.0676
03/20 12:00:00 | 24.2765 | 26.6218 | 25.8788 | 25.7196 | 25.6847 | 26.197 | 22.6379 | 31.6203 | 25.2121 | 29.541 | 31.2459 | 30.953 | 30.2842 | 2.9423 | [14 empty] | 2.685 |  | 822.4322 |  |  |  | 495.9439 |  | 707.4947 |  | 801.0989 |  | 784.6016 |  | 747.5802
03/20 13:00:00 | 24.3997 | 26.7254 | 25.8955 | 25.6879 | 25.6874 | 26.2126 | 22.6228 | 29.4216 | 22.4041 | 26.9427 | 28.7402 | 28.2981 | 27.3769 | 2.8888 | [14 empty] | 3.1576 |  | 703.9929 |  |  |  | 380.8472 |  | 578.5921 |  | 668.2984 |  | 645.6341 |  | 599.6681
03/20 14:00:00 | 24.5889 | 26.8618 | 26.0595 | 25.7782 | 25.8192 | 26.3866 | 22.6715 | 27.2034 | 18.8616 | 24.5195 | 26.1962 | 25.663 | 24.8141 | 2.8473 | [14 empty] | 3.6762 |  | 593.2196 |  |  |  | 256.4582 |  | 469.686 |  | 545.1723 |  | 520.5571 |  | 482.5424
03/20 15:00:00 | 25.0173 | 27.3064 | 26.5448 | 26.1555 | 26.2656 | 26.8446 | 22.7997 | 24.0878 | 15.3098 | 21.7303 | 23.035 | 22.5847 | 21.3609 | 2.8416 | [14 empty] | 4.9177 |  | 451.3993 |  |  |  | 155.4569 |  | 356.7818 |  | 407.7749 |  | 389.7912 |  | 342.964
03/20 16:00:00 | 25.3938 | 27.6753 | 26.9785 | 26.4915 | 26.6366 | 27.2202 | 22.8661 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3867 | [14 empty] | 6.3892 |  | 1.923 |  |  |  | 1.923 |  | 1.923 |  | 1.923 |  | 1.923 |  | 1.923
03/20 17:00:00 | 25.2286 | 27.6609 | 26.8568 | 26.3769 | 26.5071 | 27.1154 | 22.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 6.3281 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/20 18:00:00 | 24.6919 | 27.2502 | 26.3924 | 25.8575 | 25.967 | 26.5992 | 22.4026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 5.2407 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/20 19:00:00 | 24.0112 | 26.4506 | 25.766 | 25.1246 | 25.1035 | 25.753 | 22.0843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.7127 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/20 20:00:00 | 23.3971 | 25.8237 | 25.1856 | 24.5389 | 24.4897 | 25.1439 | 21.808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.5252 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/20 21:00:00 | 22.9919 | 25.3359 | 24.8011 | 24.0544 | 24.0155 | 24.6722 | 21.5582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.0554 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/20 22:00:00 | 22.6745 | 24.9792 | 24.4984 | 23.7195 | 23.6023 | 24.3384 | 21.3259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.8188 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/20 23:00:00 | 22.3872 | 24.672 | 24.1864 | 23.429 | 23.2941 | 24.0443 | 21.1337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.5714 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/20 24:00:00 | 22.1822 | 24.3789 | 23.9123 | 23.1572 | 23.0256 | 23.7666 | 20.9573 | 26.5193 | 29.2886 | 26.5889 | 29.1601 | 31.1058 | 30.1928 | 2.2131 | [14 empty] | 1.5003 |  | 590.7918 |  |  |  | 733.0808 |  | 594.1818 |  | 726.1423 |  | 834.7907 |  | 782.8633
03/21 01:00:00 | 22.4336 | 24.4288 | 24.0697 | 23.2509 | 23.117 | 23.8528 | 20.7628 | 21.3728 | 18.3916 | 19.2782 | 20.2361 | 20.2433 | 20.3305 | 2.8385 | [14 empty] | 2.7919 |  | 343.5198 |  |  |  | 241.8985 |  | 270.2629 |  | 302.6747 |  | 302.925 |  | 305.9695
03/21 02:00:00 | 22.4684 | 24.3509 | 24.0664 | 23.1599 | 22.9945 | 23.7497 | 20.6413 | 15.6 | 14.4038 | 14.4598 | 15.5974 | 15.9012 | 15.7856 | 2.7628 | [14 empty] | 3.3384 |  | 164.7945 |  |  |  | 135.5137 |  | 136.8214 |  | 164.7266 |  | 172.6182 |  | 169.5938
03/21 03:00:00 | 22.4773 | 24.3338 | 24.1089 | 23.1424 | 22.961 | 23.7242 | 20.5579 | 14.988 | 13.8857 | 13.9323 | 14.9573 | 15.2072 | 15.1338 | 2.758 | [14 empty] | 3.6841 |  | 149.5739 |  |  |  | 123.8273 |  | 124.866 |  | 148.8229 |  | 154.9847 |  | 153.1616
03/21 04:00:00 | 22.4844 | 24.3369 | 24.1365 | 23.1461 | 22.9649 | 23.7224 | 20.4014 | 14.3029 | 15.6459 | 13.3691 | 16.4663 | 16.3113 | 16.4455 | 2.7332 | [14 empty] | 4.3389 |  | 133.8579 |  |  |  | 166.738 |  | 113.1228 |  | 188.5987 |  | 184.366 |  | 188.0287
03/21 05:00:00 | 22.4708 | 24.3334 | 24.138 | 23.1311 | 22.9446 | 23.6992 | 20.2962 | 13.5829 | 14.5307 | 12.7812 | 15.2202 | 15.1183 | 15.2074 | 2.7776 | [14 empty] | 4.7291 |  | 116.7541 |  |  |  | 138.1349 |  | 100.0717 |  | 154.8185 |  | 152.2927 |  | 154.4999
03/21 06:00:00 | 22.435 | 24.2939 | 24.1129 | 23.0704 | 22.8737 | 23.6269 | 20.1317 | 13.1844 | 13.9301 | 12.3718 | 14.5985 | 14.4713 | 14.5454 | 2.8286 | [14 empty] | 5.3053 |  | 107.2428 |  |  |  | 123.2444 |  | 91.0739 |  | 138.5315 |  | 135.5541 |  | 137.2846
03/21 07:00:00 | 22.3779 | 24.2121 | 24.0622 | 22.9619 | 22.7528 | 23.5068 | 20.5259 | 12.9041 | 11.5488 | 11.9873 | 12.239 | 12.5201 | 12.4155 | 76.4204 | [14 empty] | 3.4297 |  | 4034.3182 |  |  |  | 4208.3197 |  | 4151.621 |  | 4119.2437 |  | 4083.2404 |  | 4096.6263
03/21 08:00:00 | 22.3297 | 24.1371 | 24.0178 | 22.8655 | 22.6504 | 23.4039 | 21.9647 | 18.5084 | 17.6639 | 17.9144 | 17.5583 | 18.0267 | 17.7592 | 21.3274 | [14 empty] | 0.13322 |  | 7.9468 |  |  |  | 13.4217 |  | 11.6483 |  | 14.2058 |  | 10.8948 |  | 12.7323
03/21 09:00:00 | 22.4292 | 24.1897 | 24.1004 | 22.9036 | 22.7055 | 23.4386 | 22.3265 | 17.3226 | 16.1149 | 16.4977 | 16.399 | 16.4471 | 16.4791 | 12.0588 | [14 empty] | 0.010537 |  | 27.7069 |  |  |  | 16.4518 |  | 19.7032 |  | 18.8369 |  | 19.2566 |  | 19.5385
03/21 10:00:00 | 22.6846 | 24.3981 | 24.3436 | 23.093 | 22.9124 | 23.6313 | 22.3724 | 14.6605 | 14.1031 | 14.2112 | 13.6648 | 13.678 | 13.5938 | 11.6111 | [14 empty] | 0.097495 |  | 9.2988 |  |  |  | 6.2103 |  | 6.7605 |  | 4.2177 |  | 4.2721 |  | 3.9313
03/21 11:00:00 | 23.1555 | 24.9265 | 24.8319 | 23.517 | 23.3493 | 24.1326 | 22.834 | 11.4133 | 11.4648 | 11.3119 | 10.4685 | 10.4987 | 10.2797 | 3.5299 | [14 empty] | 0.10334 |  | 62.148 |  |  |  | 62.9634 |  | 60.5609 |  | 48.1451 |  | 48.5651 |  | 45.5603
03/21 12:00:00 | 23.9742 | 25.9692 | 25.7069 | 24.3092 | 24.2118 | 25.0639 | 23.1783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.63357 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/21 13:00:00 | 24.0097 | 26.2099 | 25.7926 | 24.3979 | 24.3448 | 25.212 | 23.4825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.27791 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/21 14:00:00 | 23.8925 | 26.1566 | 25.7228 | 24.3415 | 24.3229 | 25.2097 | 23.8806 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.00014049 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/21 15:00:00 | 24.3313 | 26.6349 | 26.1956 | 24.804 | 24.7946 | 25.6915 | 24.2928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.001481 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/21 16:00:00 | 24.7112 | 27.0744 | 26.6069 | 25.2142 | 25.1994 | 26.1154 | 24.6101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.010217 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/21 17:00:00 | 24.8413 | 27.2455 | 26.756 | 25.3633 | 25.3503 | 26.2888 | 24.7396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.010328 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/21 18:00:00 | 24.8761 | 27.298 | 26.784 | 25.3935 | 25.3845 | 26.346 | 24.6049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.073529 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/21 19:00:00 | 24.5163 | 26.9339 | 26.3847 | 24.9963 | 24.9882 | 25.9463 | 24.2228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.086151 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/21 20:00:00 | 23.9236 | 26.2594 | 25.7452 | 24.349 | 24.3346 | 25.2757 | 23.7159 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82714 | [14 empty] | 0.043166 |  | 0.68416 |  |  |  | 0.68416 |  | 0.68416 |  | 0.68416 |  | 0.68416 |  | 0.68416
03/21 21:00:00 | 23.4839 | 25.7272 | 25.3328 | 23.8969 | 23.8748 | 24.8114 | 23.2426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.058237 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/21 22:00:00 | 23.1777 | 25.3461 | 25.03 | 23.5898 | 23.5617 | 24.4929 | 22.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.10739 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/21 23:00:00 | 22.9482 | 25.0303 | 24.7879 | 23.3514 | 23.3177 | 24.1825 | 22.3274 | 15.0586 | 16.4317 | 15.2358 | 16.0452 | 16.8875 | 16.366 | 0 | [14 empty] | 0.38541 |  | 226.761 |  |  |  | 270.0003 |  | 232.1282 |  | 257.4474 |  | 285.1863 |  | 267.8463
03/21 24:00:00 | 22.8108 | 24.8149 | 24.6088 | 23.1507 | 23.0981 | 23.9564 | 21.7076 | 11.8443 | 10.1714 | 10.7853 | 10.8407 | 10.7422 | 10.7478 | 3.7404 | [14 empty] | 1.217 |  | 65.6736 |  |  |  | 41.3574 |  | 49.6311 |  | 50.4148 |  | 49.0256 |  | 49.1033
03/22 01:00:00 | 22.6024 | 24.5081 | 24.2922 | 22.8107 | 22.7305 | 23.6193 | 20.5753 | 9.4713 | 8.2032 | 8.5624 | 9.0886 | 9.0563 | 9.075 | 2.9627 | [14 empty] | 4.1088 |  | 42.3621 |  |  |  | 27.4629 |  | 31.3569 |  | 37.5262 |  | 37.1314 |  | 37.3596
03/22 02:00:00 | 22.5252 | 24.3749 | 24.168 | 22.6808 | 22.5876 | 23.4854 | 19.7784 | 10.9741 | 9.4178 | 10.1027 | 9.9372 | 9.7599 | 9.8131 | 3.0934 | [14 empty] | 7.5444 |  | 62.1058 |  |  |  | 39.9986 |  | 49.1308 |  | 46.8382 |  | 44.4425 |  | 45.1553
03/22 03:00:00 | 22.212 | 24.0554 | 23.8285 | 22.3263 | 22.221 | 23.1262 | 19.1165 | 11.1111 | 9.2594 | 10.0627 | 10.1403 | 9.9846 | 10.0343 | 23.8574 | [14 empty] | 9.5824 |  | 162.4686 |  |  |  | 213.1016 |  | 190.2937 |  | 188.1595 |  | 192.4565 |  | 191.0778
03/22 04:00:00 | 21.8231 | 23.6387 | 23.4079 | 21.8897 | 21.7684 | 22.6806 | 18.5162 | 11.4879 | 9.3711 | 10.3129 | 10.5577 | 10.4098 | 10.4626 | 21.1195 | [14 empty] | 10.9359 |  | 92.7679 |  |  |  | 138.0242 |  | 116.7825 |  | 111.5507 |  | 114.6973 |  | 113.5689
03/22 05:00:00 | 21.4371 | 23.2226 | 22.9944 | 21.4693 | 21.3327 | 22.2484 | 18.5008 | 11.0307 | 9.2758 | 10.0475 | 10.2122 | 10.0893 | 10.1302 | 20.1602 | [14 empty] | 8.6216 |  | 83.3487 |  |  |  | 118.4704 |  | 102.2667 |  | 98.9641 |  | 101.4236 |  | 100.6024
03/22 06:00:00 | 21.1384 | 22.8918 | 22.6771 | 21.1483 | 21.0001 | 21.9185 | 18.4433 | 11.1137 | 9.225 | 10.0612 | 10.2943 | 10.1666 | 10.2121 | 21.9018 | [14 empty] | 7.2635 |  | 116.3834 |  |  |  | 160.7027 |  | 140.1999 |  | 134.7338 |  | 137.715 |  | 136.6489
03/22 07:00:00 | 20.8094 | 22.5292 | 22.3291 | 20.7931 | 20.6318 | 21.5529 | 18.8709 | 10.6741 | 9.0205 | 9.7589 | 9.951 | 9.8417 | 9.8766 | 87.5793 | [14 empty] | 3.7578 |  | 5914.4141 |  |  |  | 6171.4861 |  | 6056.0097 |  | 6026.1571 |  | 6043.1422 |  | 6037.7125
03/22 08:00:00 | 20.5351 | 22.2169 | 22.0395 | 20.4942 | 20.3215 | 21.2457 | 20.4747 | 28.7879 | 10.4375 | 11.8131 | 34.2331 | 37.3384 | 13.1607 | 60.1867 | [14 empty] | 0.0036458 |  | 985.8877 |  |  |  | 2474.9894 |  | 2340.0076 |  | 673.5905 |  | 522.0464 |  | 2211.4487
03/22 09:00:00 | 20.6668 | 22.1883 | 22.0431 | 20.631 | 20.4734 | 21.2461 | 21.8014 | 47.5077 | 11.3855 | 30.1176 | 56.8501 | 59.5409 | 37.7803 | 25.0311 | [14 empty] | 1.2873 |  | 505.1983 |  |  |  | 186.2017 |  | 25.8725 |  | 1012.4501 |  | 1190.9288 |  | 162.5428
03/22 10:00:00 | 21.6497 | 22.3463 | 22.4709 | 22.2837 | 22.1717 | 21.7437 | 22.0327 | 40.1568 | 10.5179 | 22.8872 | 36.3598 | 41.1982 | 42.3693 | 12.4462 | [14 empty] | 0.14671 |  | 767.879 |  |  |  | 3.7185 |  | 109.0152 |  | 571.8605 |  | 826.6768 |  | 895.3907
03/22 11:00:00 | 23.3679 | 23.2498 | 23.8109 | 24.6403 | 24.7046 | 23.9034 | 22.3024 | 32.1785 | 7.0241 | 16.8485 | 28.4638 | 29.6651 | 26.7874 | 6.7814 | [14 empty] | 1.1353 |  | 645.0101 |  |  |  | 0.058904 |  | 101.345 |  | 470.1241 |  | 523.6631 |  | 400.2387
03/22 12:00:00 | 24.9998 | 24.3518 | 24.9277 | 25.8328 | 26.077 | 26.0741 | 22.3409 | 28.223 | 5.8767 | 15.0938 | 25.5904 | 27.2824 | 21.6171 | 3.3529 | [14 empty] | 7.07 |  | 618.5238 |  |  |  | 6.3694 |  | 137.8499 |  | 494.5065 |  | 572.6201 |  | 333.5808
03/22 13:00:00 | 25.3177 | 24.5644 | 25.0695 | 25.9586 | 26.226 | 26.2968 | 22.2764 | 26.2483 | 5.2525 | 14.1223 | 23.5294 | 24.65 | 20.0379 | 31.1723 | [14 empty] | 9.2496 |  | 24.2457 |  |  |  | 671.8357 |  | 290.7011 |  | 58.414 |  | 42.5397 |  | 123.9749
03/22 14:00:00 | 25.4573 | 24.7065 | 25.2059 | 26.1205 | 26.3932 | 26.4678 | 22.4396 | 24.043 | 4.4291 | 12.9779 | 21.1009 | 21.0696 | 17.5319 | 12.4006 | [14 empty] | 9.1062 |  | 135.547 |  |  |  | 63.5445 |  | 0.33328 |  | 75.696 |  | 75.1517 |  | 26.3303
03/22 15:00:00 | 25.9902 | 25.2976 | 25.7856 | 26.6538 | 26.9255 | 27.0222 | 22.7115 | 21.4196 | 3.7004 | 11.5182 | 17.7207 | 17.3119 | 14.3713 | 3.5476 | [14 empty] | 10.7493 |  | 319.4117 |  |  |  | 0.023366 |  | 63.531 |  | 200.8772 |  | 189.4565 |  | 117.1527
03/22 16:00:00 | 26.4155 | 25.8154 | 26.2647 | 27.148 | 27.3204 | 27.4707 | 22.7061 | 18.4097 | 2.8376 | 10.0114 | 14.7813 | 14.1292 | 11.2573 | 22.5324 | [14 empty] | 13.7597 |  | 16.9963 |  |  |  | 387.8825 |  | 156.7742 |  | 60.0796 |  | 70.614 |  | 127.1266
03/22 17:00:00 | 26.6274 | 26.1129 | 26.5127 | 27.3585 | 27.5245 | 27.7248 | 22.8846 | 17.0344 | 2.8174 | 9.0693 | 13.7688 | 13.7346 | 10.508 | 3.5286 | [14 empty] | 14.0082 |  | 182.4072 |  |  |  | 0.5058 |  | 30.6994 |  | 104.8631 |  | 104.1622 |  | 48.7126
03/22 18:00:00 | 26.7018 | 26.3131 | 26.6349 | 27.441 | 27.6313 | 27.874 | 22.7252 | 17.7638 | 3.0237 | 9.2961 | 14.9466 | 16.4655 | 12.3319 | 11.8927 | [14 empty] | 15.8128 |  | 34.4693 |  |  |  | 78.66 |  | 6.7423 |  | 9.3264 |  | 20.9098 |  | 0.19284
03/22 19:00:00 | 26.4303 | 26.1532 | 26.3588 | 27.1818 | 27.3693 | 27.6914 | 22.4677 | 21.0814 | 4.6996 | 11.603 | 19.7793 | 22.3325 | 17.6739 | 19.6986 | [14 empty] | 15.7018 |  | 1.912 |  |  |  | 224.97 |  | 65.5398 |  | 0.0065064 |  | 6.937 |  | 4.0997
03/22 20:00:00 | 25.9576 | 25.4165 | 25.7627 | 26.6264 | 26.842 | 27.0503 | 22.0322 | 22.1009 | 6.0666 | 12.9121 | 20.7928 | 23.6347 | 19.0928 | 4.1312 | [14 empty] | 15.4088 |  | 322.9072 |  |  |  | 3.7456 |  | 77.1029 |  | 277.608 |  | 380.3842 |  | 223.8497
03/22 21:00:00 | 25.3902 | 24.6296 | 25.123 | 26.0577 | 26.2591 | 26.3923 | 21.3584 | 18.6403 | 5.6064 | 10.8705 | 16.6916 | 18.4586 | 15.3597 | 3.416 | [14 empty] | 16.2554 |  | 231.7791 |  |  |  | 4.798 |  | 55.5694 |  | 176.2413 |  | 226.2793 |  | 142.652
03/22 22:00:00 | 24.927 | 24.0299 | 24.6094 | 25.5749 | 25.8014 | 25.8775 | 20.6852 | 18.1875 | 5.8788 | 10.8432 | 16.3658 | 17.9703 | 15.0909 | 3.1871 | [14 empty] | 17.9926 |  | 225.0138 |  |  |  | 7.2452 |  | 58.616 |  | 173.6791 |  | 218.5454 |  | 141.7017
03/22 23:00:00 | 24.5346 | 23.5408 | 24.1043 | 25.0696 | 25.2931 | 25.4064 | 20.0498 | 17.6909 | 6.0115 | 10.7543 | 16.0163 | 17.553 | 14.7987 | 3.1052 | [14 empty] | 20.1138 |  | 212.7435 |  |  |  | 8.4465 |  | 58.5084 |  | 166.697 |  | 208.7403 |  | 136.7386
03/22 24:00:00 | 24.127 | 23.0462 | 23.6942 | 24.5538 | 24.6814 | 24.8971 | 19.5229 | 16.921 | 6.0144 | 10.4554 | 15.377 | 16.8227 | 14.2336 | 20.9899 | [14 empty] | 21.1973 |  | 16.5557 |  |  |  | 224.264 |  | 110.9751 |  | 31.5051 |  | 17.3658 |  | 45.6478
03/23 01:00:00 | 23.7484 | 22.6675 | 23.3287 | 24.1591 | 24.153 | 24.5006 | 19.2623 | 13.5176 | 5.77 | 8.5149 | 14.6154 | 16.0884 | 12.2076 | 17.3981 | [14 empty] | 20.1252 |  | 15.0585 |  |  |  | 135.2139 |  | 78.9115 |  | 7.7438 |  | 1.7153 |  | 26.9414
03/23 02:00:00 | 23.5688 | 22.4917 | 23.1738 | 23.9891 | 23.9668 | 24.3226 | 19.1042 | 15.8311 | 5.7458 | 9.9948 | 14.064 | 15.4156 | 13.3268 | 18.5361 | [14 empty] | 19.9328 |  | 7.3172 |  |  |  | 163.5911 |  | 72.9532 |  | 19.9998 |  | 9.7375 |  | 27.1368
03/23 03:00:00 | 23.2615 | 22.1239 | 22.8684 | 23.5723 | 23.5777 | 23.9232 | 18.9668 | 15.5797 | 5.9201 | 9.9215 | 14.2177 | 15.5129 | 13.3073 | 18.5728 | [14 empty] | 18.4443 |  | 8.959 |  |  |  | 160.0902 |  | 74.8459 |  | 18.9674 |  | 9.3631 |  | 27.7256
03/23 04:00:00 | 22.9021 | 21.7032 | 22.4454 | 23.0995 | 23.1154 | 23.4459 | 18.7902 | 14.0286 | 5.6997 | 9.1424 | 12.8491 | 14.0955 | 11.9654 | 20.0966 | [14 empty] | 16.9081 |  | 36.8208 |  |  |  | 207.2698 |  | 119.9948 |  | 52.5266 |  | 36.0133 |  | 66.1169
03/23 05:00:00 | 22.5962 | 21.4066 | 22.1445 | 22.7666 | 22.7813 | 23.1118 | 18.6432 | 13.4256 | 5.4958 | 8.7814 | 12.2569 | 13.4497 | 11.4333 | 20.8304 | [14 empty] | 15.6264 |  | 54.8304 |  |  |  | 235.151 |  | 145.1791 |  | 73.5043 |  | 54.474 |  | 88.3049
03/23 06:00:00 | 22.2906 | 21.1382 | 21.8683 | 22.4558 | 22.4626 | 22.7956 | 18.5385 | 12.9925 | 5.4004 | 8.5523 | 11.8846 | 13.018 | 11.0957 | 21.4412 | [14 empty] | 14.0785 |  | 71.3814 |  |  |  | 257.3076 |  | 166.1248 |  | 91.3289 |  | 70.9504 |  | 107.0299
03/23 07:00:00 | 21.9859 | 20.8668 | 21.5936 | 22.142 | 22.137 | 22.4803 | 19.005 | 12.9963 | 5.3865 | 8.5511 | 11.919 | 12.9842 | 11.134 | 79.6733 | [14 empty] | 8.8855 |  | 4445.8127 |  |  |  | 5518.5227 |  | 5058.362 |  | 4590.6413 |  | 4447.4351 |  | 4697.6371
03/23 08:00:00 | 21.717 | 20.6241 | 21.3528 | 21.8563 | 21.8359 | 22.1907 | 20.691 | 14.844 | 35.6775 | 12.2389 | 14.5419 | 16.2778 | 17.5749 | 64.156 | [14 empty] | 1.0527 |  | 2431.6767 |  |  |  | 811.0239 |  | 2695.3836 |  | 2461.5608 |  | 2292.3215 |  | 2169.801
03/23 09:00:00 | 21.7282 | 20.8688 | 21.424 | 21.8601 | 21.8336 | 22.2569 | 22.0627 | 28.643 | 48.3473 | 30.2014 | 33.2538 | 36.909 | 16.4524 | 10.3142 | [14 empty] | 0.11193 |  | 335.9441 |  |  |  | 1446.5183 |  | 395.5007 |  | 526.223 |  | 707.281 |  | 37.6772
03/23 10:00:00 | 22.2977 | 23.1897 | 22.2338 | 22.4586 | 22.5657 | 22.9863 | 22.3254 | 23.2291 | 18.8218 | 21.5139 | 24.5402 | 25.0159 | 10.4617 | 8.4178 | [14 empty] | 0.00076535 |  | 219.3727 |  |  |  | 108.2422 |  | 171.5076 |  | 259.9306 |  | 275.4948 |  | 4.1773
03/23 11:00:00 | 23.8078 | 26.3436 | 24.1342 | 24.4615 | 24.7146 | 24.2695 | 22.4966 | 18.0129 | 13.6153 | 16.2259 | 17.5994 | 17.5221 | 8.8898 | 3.3769 | [14 empty] | 1.7194 |  | 214.2124 |  |  |  | 104.8266 |  | 165.0987 |  | 202.2795 |  | 200.0874 |  | 30.3929
03/23 12:00:00 | 25.0378 | 27.4818 | 25.42 | 25.6676 | 25.9055 | 25.3858 | 22.6319 | 16.1562 | 15.8276 | 14.9076 | 16.0952 | 16.2212 | 7.6818 | 3.0674 | [14 empty] | 5.7882 |  | 171.3171 |  |  |  | 162.823 |  | 140.1915 |  | 169.724 |  | 173.0222 |  | 21.293
03/23 13:00:00 | 25.2457 | 27.5504 | 25.6367 | 25.835 | 26.0941 | 25.5274 | 22.774 | 14.7048 | 9.4888 | 13.5009 | 14.6392 | 14.9172 | 6.5114 | 2.9418 | [14 empty] | 6.1092 |  | 138.3677 |  |  |  | 42.8632 |  | 111.4941 |  | 136.8305 |  | 143.4099 |  | 12.7422
03/23 14:00:00 | 25.5289 | 27.8266 | 25.9607 | 26.1518 | 26.3396 | 25.859 | 22.8801 | 14.3104 | 5.6312 | 12.7842 | 14.0741 | 13.9385 | 6.3891 | 2.7822 | [14 empty] | 7.0162 |  | 132.8974 |  |  |  | 8.1166 |  | 100.04 |  | 127.5051 |  | 124.4623 |  | 13.0094
03/23 15:00:00 | 26.1319 | 28.3708 | 26.6201 | 26.7889 | 26.9513 | 26.5131 | 23.1307 | 12.748 | 4.0045 | 11.3107 | 11.9145 | 11.8857 | 5.0867 | 2.7691 | [14 empty] | 9.007 |  | 99.5783 |  |  |  | 1.5262 |  | 72.9595 |  | 83.638 |  | 83.1118 |  | 5.3715
03/23 16:00:00 | 26.5918 | 28.7619 | 27.1252 | 27.2828 | 27.4302 | 27.021 | 23.3805 | 11.5812 | 3.2339 | 9.5844 | 10.1645 | 10.1261 | 4.9915 | 2.7528 | [14 empty] | 10.3124 |  | 77.9406 |  |  |  | 0.23144 |  | 46.6706 |  | 54.9323 |  | 54.3652 |  | 5.0118
03/23 17:00:00 | 26.8439 | 28.9906 | 27.4037 | 27.5512 | 27.7017 | 27.335 | 23.4887 | 10.5372 | 3.0288 | 8.6773 | 9.2616 | 9.2407 | 4.2438 | 2.7278 | [14 empty] | 11.2577 |  | 60.9872 |  |  |  | 0.090595 |  | 35.3968 |  | 42.6911 |  | 42.4176 |  | 2.2982
03/23 18:00:00 | 26.998 | 29.1581 | 27.5546 | 27.7181 | 27.8664 | 27.556 | 23.5636 | 10.9974 | 5.2165 | 9.1075 | 9.6283 | 9.6318 | 4.8251 | 2.78 | [14 empty] | 11.7954 |  | 67.525 |  |  |  | 5.9362 |  | 40.0369 |  | 46.8992 |  | 46.9461 |  | 4.1822
03/23 19:00:00 | 26.8383 | 29.0293 | 27.3727 | 27.581 | 27.7199 | 27.4462 | 23.2384 | 13.1611 | 13.6347 | 11.6426 | 13.0431 | 13.3715 | 7.3974 | 2.8585 | [14 empty] | 12.9592 |  | 106.1453 |  |  |  | 116.1264 |  | 77.1607 |  | 103.7265 |  | 110.5246 |  | 20.602
03/23 20:00:00 | 26.3259 | 28.4956 | 26.8044 | 27.0665 | 27.1577 | 26.8372 | 22.6606 | 13.3744 | 16.7554 | 11.9981 | 13.0515 | 13.308 | 7.9321 | 2.9934 | [14 empty] | 13.4344 |  | 107.7643 |  |  |  | 189.3935 |  | 81.0851 |  | 101.1655 |  | 106.3917 |  | 24.3909
03/23 21:00:00 | 25.8259 | 27.975 | 26.2911 | 26.5538 | 26.6395 | 26.252 | 22.134 | 10.8426 | 15.1437 | 9.4342 | 10.1186 | 10.2989 | 6.6539 | 2.924 | [14 empty] | 13.6302 |  | 62.7039 |  |  |  | 149.3193 |  | 42.382 |  | 51.7616 |  | 54.388 |  | 13.9116
03/23 22:00:00 | 25.4855 | 27.7031 | 25.9516 | 26.1425 | 26.212 | 25.8235 | 21.6829 | 10.484 | 15.6295 | 9.1811 | 9.8215 | 9.9906 | 6.4969 | 2.9562 | [14 empty] | 14.4602 |  | 56.6674 |  |  |  | 160.6126 |  | 38.7495 |  | 47.1326 |  | 49.4834 |  | 12.5367
03/23 23:00:00 | 25.1738 | 27.5169 | 25.6415 | 25.8358 | 25.874 | 25.4925 | 21.2858 | 10.2621 | 15.531 | 9.011 | 9.6358 | 9.7914 | 6.4654 | 2.889 | [14 empty] | 15.1169 |  | 54.3621 |  |  |  | 159.8201 |  | 37.4779 |  | 45.5195 |  | 47.643 |  | 12.7902
03/23 24:00:00 | 24.8631 | 27.342 | 25.3303 | 25.5281 | 25.526 | 25.1607 | 21.0026 | 9.9798 | 14.7747 | 8.849 | 9.4509 | 9.6165 | 6.4222 | 2.8673 | [14 empty] | 14.9041 |  | 50.5865 |  |  |  | 141.7851 |  | 35.7803 |  | 43.3435 |  | 45.5511 |  | 12.6371
03/24 01:00:00 | 24.6309 | 27.1708 | 25.0487 | 25.2394 | 25.1967 | 24.85 | 20.6619 | 11.7848 | 15.2541 | 10.0128 | 11.1647 | 11.3324 | 8.237 | 2.8421 | [14 empty] | 15.7533 |  | 79.9709 |  |  |  | 154.0576 |  | 51.4184 |  | 69.2652 |  | 72.0841 |  | 29.1042
03/24 02:00:00 | 23.815 | 26.4849 | 24.2192 | 24.3157 | 24.2156 | 23.9067 | 20.3609 | 10.6274 | 14.8291 | 9.4286 | 10.1902 | 10.3723 | 7.3334 | 2.9248 | [14 empty] | 11.9306 |  | 59.3299 |  |  |  | 141.7113 |  | 42.2991 |  | 52.7851 |  | 55.4643 |  | 19.4353
03/24 03:00:00 | 23.3859 | 26.1272 | 23.824 | 23.8824 | 23.7412 | 23.4803 | 20.1123 | 8.4002 | 14.0125 | 7.497 | 9.5017 | 9.6961 | 6.7881 | 2.8988 | [14 empty] | 10.7167 |  | 30.2649 |  |  |  | 123.5135 |  | 21.1429 |  | 43.5973 |  | 46.2026 |  | 15.1261
03/24 04:00:00 | 23.2986 | 26.0908 | 23.7615 | 23.8422 | 23.6858 | 23.4459 | 20.0093 | 9.8191 | 13.3899 | 8.7749 | 9.1471 | 9.3356 | 6.5431 | 2.8663 | [14 empty] | 10.8197 |  | 48.342 |  |  |  | 110.7473 |  | 34.9114 |  | 39.4492 |  | 41.8517 |  | 13.519
03/24 05:00:00 | 23.2251 | 26.0254 | 23.6997 | 23.7473 | 23.5775 | 23.3513 | 19.8383 | 8.9577 | 12.8214 | 8.1087 | 8.5196 | 8.7011 | 6.1011 | 2.9157 | [14 empty] | 11.4702 |  | 36.5051 |  |  |  | 98.1211 |  | 26.9666 |  | 31.4033 |  | 33.4701 |  | 10.1467
03/24 06:00:00 | 23.0528 | 25.8889 | 23.5394 | 23.57 | 23.3853 | 23.1787 | 19.6022 | 9.3118 | 12.536 | 8.2214 | 8.8565 | 9.0223 | 6.4906 | 16.261 | [14 empty] | 11.9068 |  | 48.2925 |  |  |  | 13.8759 |  | 64.6364 |  | 54.8277 |  | 52.3993 |  | 95.4616
03/24 07:00:00 | 22.8415 | 25.7038 | 23.334 | 23.3445 | 23.144 | 22.9568 | 20.1098 | 7.9616 | 10.6079 | 6.9724 | 8.0111 | 8.2169 | 6.0268 | 81.9942 | [14 empty] | 7.4624 |  | 5480.8286 |  |  |  | 5096.0151 |  | 5628.2722 |  | 5473.4983 |  | 5443.0925 |  | 5771.0451
03/24 08:00:00 | 22.6963 | 25.5652 | 23.1944 | 23.1911 | 22.9776 | 22.807 | 21.7387 | 10.4826 | 15.837 | 9.6449 | 9.7852 | 10.1015 | 6.6805 | 35.8544 | [14 empty] | 0.91701 |  | 643.7288 |  |  |  | 400.6948 |  | 686.9402 |  | 679.6045 |  | 663.2144 |  | 851.1181
03/24 09:00:00 | 22.775 | 25.616 | 23.2858 | 23.2484 | 23.0188 | 22.8701 | 22.4508 | 8.0421 | 13.5036 | 7.5941 | 7.3763 | 7.7279 | 4.4318 | 16.3438 | [14 empty] | 0.10515 |  | 68.9183 |  |  |  | 8.0669 |  | 76.5579 |  | 80.4153 |  | 74.2329 |  | 141.8954
03/24 10:00:00 | 23.1602 | 26.014 | 23.7221 | 23.6281 | 23.3878 | 23.2597 | 22.797 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9204 | [14 empty] | 0.13189 |  | 8.5287 |  |  |  | 8.5287 |  | 8.5287 |  | 8.5287 |  | 8.5287 |  | 8.5287
03/24 11:00:00 | 23.7548 | 26.5927 | 24.4047 | 24.2442 | 24.011 | 24.0211 | 22.8859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.75499 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/24 12:00:00 | 24.5031 | 27.3711 | 25.3275 | 25.0715 | 24.9182 | 25.0918 | 23.1083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.9455 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/24 13:00:00 | 24.7541 | 27.6167 | 25.6163 | 25.3389 | 25.2081 | 25.4497 | 23.4664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.6581 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/24 14:00:00 | 25.1135 | 27.9645 | 26.0012 | 25.7283 | 25.6103 | 25.9313 | 23.9646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.3201 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/24 15:00:00 | 25.7479 | 28.6156 | 26.6623 | 26.3633 | 26.2976 | 26.6545 | 24.4604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.6576 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/24 16:00:00 | 26.3157 | 29.2033 | 27.2751 | 26.9528 | 26.8803 | 27.268 | 24.9187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.9517 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/24 17:00:00 | 26.6563 | 29.553 | 27.6317 | 27.3037 | 27.2146 | 27.6319 | 25.4107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.5516 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/24 18:00:00 | 26.8027 | 29.6917 | 27.7617 | 27.4426 | 27.352 | 27.7903 | 25.7652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.0764 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/24 19:00:00 | 26.6904 | 29.5815 | 27.6124 | 27.3173 | 27.2166 | 27.6705 | 25.7526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.87952 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/24 20:00:00 | 26.4359 | 29.2692 | 27.2956 | 27.023 | 26.9059 | 27.3426 | 25.5146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.84875 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/24 21:00:00 | 26.1535 | 28.8629 | 26.945 | 26.6865 | 26.5506 | 26.9519 | 25.2696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.78119 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/24 22:00:00 | 25.9067 | 28.5746 | 26.6994 | 26.4483 | 26.2975 | 26.7068 | 25.0742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.69311 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/24 23:00:00 | 25.7334 | 28.336 | 26.5278 | 26.2802 | 26.1176 | 26.507 | 24.8777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.73227 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/24 24:00:00 | 25.577 | 28.1368 | 26.3672 | 26.1219 | 25.9487 | 26.3413 | 24.6857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.79439 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 01:00:00 | 25.4442 | 27.943 | 26.2273 | 25.9811 | 25.7971 | 26.1815 | 24.521 | 8.6274 | 14.7722 | 8.0322 | 9.2497 | 9.9845 | 6.3474 | 0 | [14 empty] | 0.85242 |  | 74.4325 |  |  |  | 218.2176 |  | 64.517 |  | 85.5574 |  | 99.6898 |  | 40.289
03/25 02:00:00 | 24.7265 | 27.2609 | 25.386 | 25.0658 | 24.8429 | 25.205 | 24.3904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.11293 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 03:00:00 | 24.3724 | 26.8801 | 25.005 | 24.6635 | 24.4225 | 24.7855 | 24.3013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.0050516 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 04:00:00 | 24.3392 | 26.809 | 25.0004 | 24.6767 | 24.4352 | 24.8045 | 24.2136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.015771 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 05:00:00 | 24.2973 | 26.7202 | 24.9616 | 24.6465 | 24.4017 | 24.7776 | 24.1182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.032077 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 06:00:00 | 24.2477 | 26.6206 | 24.9113 | 24.6034 | 24.355 | 24.7374 | 24.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.04752 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 07:00:00 | 24.2029 | 26.5409 | 24.8633 | 24.5589 | 24.307 | 24.6932 | 23.9458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.066135 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 08:00:00 | 24.1443 | 26.4146 | 24.8016 | 24.4992 | 24.2196 | 24.6102 | 23.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.046267 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 09:00:00 | 24.1014 | 26.2832 | 24.7546 | 24.4544 | 24.1461 | 24.5459 | 24.1791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.0060521 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 10:00:00 | 24.1463 | 26.267 | 24.8015 | 24.5019 | 24.2173 | 24.6439 | 24.599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.20502 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 11:00:00 | 24.3838 | 26.5123 | 25.0842 | 24.7588 | 24.5174 | 25.0414 | 25.0873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.49491 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 12:00:00 | 24.5722 | 26.7421 | 25.3197 | 24.9808 | 24.7707 | 25.3432 | 25.4278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.73216 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 13:00:00 | 24.6685 | 26.8414 | 25.4312 | 25.0943 | 24.8921 | 25.4677 | 25.7293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.1253 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 14:00:00 | 24.7937 | 26.955 | 25.5648 | 25.2285 | 25.0201 | 25.6064 | 26.1145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.7445 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 15:00:00 | 25.031 | 27.2314 | 25.8351 | 25.4964 | 25.2875 | 25.8993 | 26.518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.2111 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 16:00:00 | 25.2274 | 27.4629 | 26.0519 | 25.7108 | 25.5034 | 26.1358 | 26.8162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.5241 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 17:00:00 | 25.3702 | 27.5972 | 26.1946 | 25.852 | 25.647 | 26.2929 | 27.0479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.8146 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 18:00:00 | 25.4768 | 27.7138 | 26.3116 | 25.967 | 25.7642 | 26.4209 | 27.1394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.7644 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 19:00:00 | 25.5187 | 27.7645 | 26.3647 | 26.0192 | 25.8098 | 26.4697 | 27.1342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.6096 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 20:00:00 | 25.4989 | 27.7134 | 26.3204 | 25.9753 | 25.7632 | 26.4095 | 27.0024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.2606 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 21:00:00 | 25.4111 | 27.572 | 26.207 | 25.8625 | 25.6451 | 26.259 | 26.8171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.9767 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 22:00:00 | 25.3117 | 27.4144 | 26.0605 | 25.716 | 25.4923 | 26.101 | 26.6524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.7974 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 23:00:00 | 25.1981 | 27.2678 | 25.9219 | 25.5766 | 25.3473 | 25.9549 | 26.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.6128 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/25 24:00:00 | 25.0796 | 27.1269 | 25.7903 | 25.4442 | 25.2093 | 25.8153 | 26.2636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.4019 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 01:00:00 | 24.9761 | 26.9689 | 25.6441 | 25.2967 | 25.056 | 25.6593 | 25.9761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.99985 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 02:00:00 | 24.9108 | 26.8539 | 25.5432 | 25.1952 | 24.9499 | 25.5499 | 25.7215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.65736 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 03:00:00 | 24.7139 | 26.6432 | 25.3411 | 24.9905 | 24.7372 | 25.3348 | 25.4712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.57348 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 04:00:00 | 24.4947 | 26.4372 | 25.1477 | 24.7643 | 24.5357 | 25.1305 | 25.2512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.5722 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 05:00:00 | 24.3029 | 26.2697 | 24.9918 | 24.5364 | 24.372 | 24.965 | 25.0506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.55906 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 06:00:00 | 24.1659 | 26.1005 | 24.8379 | 24.3627 | 24.2107 | 24.8015 | 24.8294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.44029 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 07:00:00 | 24.0602 | 25.9286 | 24.7207 | 24.2577 | 24.0469 | 24.6358 | 24.6317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.32658 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 08:00:00 | 23.9197 | 25.7089 | 24.6071 | 24.118 | 23.8426 | 24.4324 | 24.553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.40102 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 09:00:00 | 23.832 | 25.603 | 24.5509 | 24.0332 | 23.7572 | 24.3551 | 24.0301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.039235 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 10:00:00 | 23.7979 | 25.5488 | 24.503 | 24.0076 | 23.7341 | 24.3526 | 24.0109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.04538 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 11:00:00 | 23.8793 | 25.6323 | 24.5835 | 24.1118 | 23.8589 | 24.5367 | 24.2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.10452 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 12:00:00 | 24.0444 | 25.8603 | 24.7785 | 24.3158 | 24.0769 | 24.804 | 24.1438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.0098792 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 13:00:00 | 24.2401 | 26.1102 | 25.014 | 24.549 | 24.3161 | 25.0792 | 24.2344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.2664e-05 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 14:00:00 | 24.3623 | 26.2697 | 25.137 | 24.6686 | 24.4392 | 25.2342 | 24.1957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.02774 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 15:00:00 | 24.3844 | 26.3194 | 25.1576 | 24.6864 | 24.4578 | 25.27 | 24.5096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.015675 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 16:00:00 | 24.352 | 26.2889 | 25.1129 | 24.6389 | 24.4091 | 25.2188 | 24.6222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.072983 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 17:00:00 | 24.3224 | 26.2552 | 25.0716 | 24.596 | 24.365 | 25.1758 | 24.7677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.19837 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 18:00:00 | 24.3204 | 26.2563 | 25.07 | 24.5928 | 24.3625 | 25.182 | 24.6876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.13485 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 19:00:00 | 24.1755 | 26.1086 | 24.9233 | 24.4416 | 24.2075 | 25.0134 | 24.4154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.057547 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 20:00:00 | 23.9146 | 25.8119 | 24.6516 | 24.1663 | 23.9248 | 24.6927 | 24.1403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.050933 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 21:00:00 | 23.6816 | 25.553 | 24.405 | 23.9174 | 23.6688 | 24.4345 | 23.9656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.080655 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 22:00:00 | 23.508 | 25.3656 | 24.2197 | 23.7302 | 23.4756 | 24.2503 | 23.8066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.089118 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 23:00:00 | 23.3444 | 25.1526 | 24.0442 | 23.5525 | 23.2918 | 24.0692 | 23.6737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.10842 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/26 24:00:00 | 23.1792 | 24.9442 | 23.8672 | 23.3725 | 23.1056 | 23.8829 | 23.5633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.14755 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 01:00:00 | 23.0102 | 24.7559 | 23.6867 | 23.1885 | 22.915 | 23.6905 | 23.4844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.22488 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 02:00:00 | 23.0033 | 24.71 | 23.6712 | 23.1729 | 22.895 | 23.6636 | 23.3032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.089936 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 03:00:00 | 22.91 | 24.5897 | 23.5609 | 23.0661 | 22.7826 | 23.541 | 23.1014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.036636 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 04:00:00 | 22.7842 | 24.4389 | 23.4258 | 22.9251 | 22.6361 | 23.3899 | 22.9424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.025023 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 05:00:00 | 22.6908 | 24.3261 | 23.3261 | 22.8202 | 22.5267 | 23.2776 | 22.8319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.019915 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 06:00:00 | 22.6292 | 24.2498 | 23.2595 | 22.7501 | 22.4535 | 23.2018 | 22.7794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.022571 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 07:00:00 | 22.5611 | 24.1675 | 23.1862 | 22.673 | 22.373 | 23.1189 | 22.7211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.025604 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 08:00:00 | 22.5234 | 24.1102 | 23.1438 | 22.6262 | 22.3234 | 23.0651 | 22.9076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.1476 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 09:00:00 | 22.695 | 24.2166 | 23.3223 | 22.7872 | 22.4843 | 23.2328 | 23.3192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.38961 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 10:00:00 | 23.1954 | 24.7104 | 23.8484 | 23.2799 | 22.9821 | 23.805 | 23.8116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.37969 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 11:00:00 | 23.8368 | 25.4774 | 24.5819 | 23.9719 | 23.6848 | 24.5496 | 24.3173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.23081 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 12:00:00 | 24.4764 | 26.2912 | 25.3291 | 24.6797 | 24.3987 | 25.2807 | 24.7786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.091368 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 13:00:00 | 24.7111 | 26.6082 | 25.5264 | 24.8728 | 24.6483 | 25.5117 | 25.2167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.25571 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 14:00:00 | 24.9084 | 26.8885 | 25.7237 | 25.0679 | 24.8482 | 25.7716 | 25.6061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.48686 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 15:00:00 | 25.545 | 27.6337 | 26.4209 | 25.7438 | 25.5412 | 26.5145 | 26.0207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.2263 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 16:00:00 | 26.0708 | 28.2713 | 27.0195 | 26.299 | 26.1071 | 27.1066 | 26.1886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.013895 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 17:00:00 | 26.3477 | 28.6435 | 27.3219 | 26.5635 | 26.3776 | 27.433 | 25.8871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.21221 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 18:00:00 | 26.3937 | 28.7452 | 27.3441 | 26.6297 | 26.4496 | 27.4734 | 26.1842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.043878 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 19:00:00 | 26.1996 | 28.5206 | 27.0669 | 26.3868 | 26.2058 | 27.2211 | 26.2105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.00011925 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 20:00:00 | 25.897 | 28.1389 | 26.6749 | 26.0204 | 25.8307 | 26.8258 | 25.9936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.00934 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 21:00:00 | 25.5611 | 27.7343 | 26.2871 | 25.6476 | 25.4464 | 26.4288 | 25.6997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.019197 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 22:00:00 | 25.2415 | 27.3393 | 25.9751 | 25.3437 | 25.1314 | 26.1054 | 25.4673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.051007 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 23:00:00 | 24.9411 | 27.0043 | 25.6651 | 25.0392 | 24.8152 | 25.7814 | 25.2555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.098853 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/27 24:00:00 | 24.7126 | 26.6891 | 25.425 | 24.7479 | 24.5132 | 25.4704 | 25.1219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.16752 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 01:00:00 | 24.5421 | 26.4228 | 25.2441 | 24.5598 | 24.3188 | 25.2678 | 24.9661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.17973 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 02:00:00 | 24.2497 | 26.0931 | 24.9343 | 24.2627 | 24.0145 | 24.9557 | 24.8131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.31737 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 03:00:00 | 24.0726 | 25.9082 | 24.7487 | 24.0882 | 23.8352 | 24.7689 | 24.7128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.40992 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 04:00:00 | 24.0053 | 25.8269 | 24.6773 | 24.0202 | 23.7643 | 24.6921 | 24.597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.35012 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 05:00:00 | 23.8942 | 25.6945 | 24.5585 | 23.9042 | 23.644 | 24.5641 | 24.4638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.32444 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 06:00:00 | 23.7679 | 25.5473 | 24.4233 | 23.7717 | 23.5074 | 24.42 | 24.2987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.2817 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 07:00:00 | 23.672 | 25.4373 | 24.3192 | 23.6689 | 23.4019 | 24.3096 | 24.1377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.21682 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 08:00:00 | 23.5579 | 25.3 | 24.1955 | 23.5452 | 23.2732 | 24.175 | 24.0103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.20467 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 09:00:00 | 23.5512 | 25.2377 | 24.1825 | 23.521 | 23.2437 | 24.1371 | 24.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.2635 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 10:00:00 | 23.7387 | 25.3653 | 24.3744 | 23.6945 | 23.4149 | 24.2924 | 24.2244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.23598 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 11:00:00 | 23.9976 | 25.5857 | 24.6459 | 23.949 | 23.6715 | 24.5373 | 24.3399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.11717 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 12:00:00 | 24.1735 | 25.7476 | 24.8318 | 24.1243 | 23.8502 | 24.7092 | 24.3535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.03241 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 13:00:00 | 24.0838 | 25.6801 | 24.7371 | 24.0321 | 23.7588 | 24.6181 | 24.3808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.088259 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 14:00:00 | 24.0899 | 25.6931 | 24.7425 | 24.0346 | 23.7634 | 24.6231 | 24.4305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.11601 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 15:00:00 | 24.3662 | 25.9619 | 25.0368 | 24.3121 | 24.048 | 24.9101 | 24.5137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.021762 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 16:00:00 | 24.5404 | 26.148 | 25.2246 | 24.4877 | 24.2282 | 25.0896 | 24.1923 | 0 | 0 | 0 | 0 | 0 | 0 | -0.20318 | [14 empty] | 0.12114 |  | 0.041284 |  |  |  | 0.041284 |  | 0.041284 |  | 0.041284 |  | 0.041284 |  | 0.041284
03/28 17:00:00 | 24.4931 | 26.1236 | 25.1754 | 24.438 | 24.1788 | 25.0416 | 23.9413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.30456 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 18:00:00 | 24.4172 | 26.0691 | 25.0938 | 24.3585 | 24.0992 | 24.9658 | 23.7703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.41849 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 19:00:00 | 24.1678 | 25.8483 | 24.8319 | 24.104 | 23.8422 | 24.7133 | 23.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.27968 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 20:00:00 | 23.8463 | 25.4918 | 24.4396 | 23.7206 | 23.4512 | 24.3279 | 23.2686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.33379 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 21:00:00 | 23.4921 | 25.0228 | 24.0312 | 23.2327 | 22.953 | 23.8366 | 23.1522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.1156 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/28 22:00:00 | 23.1446 | 24.6528 | 23.682 | 22.8733 | 22.5861 | 23.4735 | 23.0681 | 9.7868 | 16.9696 | 9.5534 | 11.1869 | 12.1948 | 8.2209 | 0 | [14 empty] | 0.0058621 |  | 95.7814 |  |  |  | 287.9685 |  | 91.268 |  | 125.1462 |  | 148.7128 |  | 67.583
03/28 23:00:00 | 22.9185 | 24.5017 | 23.4557 | 22.666 | 22.3714 | 23.2294 | 22.8918 | 6.4649 | 10.2538 | 5.6473 | 7.3393 | 7.5278 | 5.3049 | 0 | [14 empty] | 0.00070889 |  | 41.7952 |  |  |  | 105.1414 |  | 31.8915 |  | 53.8653 |  | 56.668 |  | 28.1419
03/28 24:00:00 | 22.7613 | 24.3711 | 23.2961 | 22.487 | 22.1883 | 23.0103 | 22.7735 | 7.6823 | 9.5743 | 6.5839 | 7.2925 | 7.3944 | 5.3363 | 0 | [14 empty] | 0.00014883 |  | 59.0174 |  |  |  | 91.6668 |  | 43.3477 |  | 53.1811 |  | 54.6778 |  | 28.4761
03/29 01:00:00 | 22.6289 | 24.2517 | 23.1541 | 22.3197 | 22.0159 | 22.8137 | 22.5539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.0056141 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/29 02:00:00 | 22.5551 | 24.1905 | 23.0921 | 22.2968 | 21.9966 | 22.7717 | 22.304 | 8.5019 | 12.3882 | 7.8452 | 8.845 | 9.2357 | 6.527 | 0 | [14 empty] | 0.063022 |  | 72.2823 |  |  |  | 153.4683 |  | 61.5472 |  | 78.2347 |  | 85.2988 |  | 42.6017
03/29 03:00:00 | 22.3553 | 24.0244 | 22.8843 | 22.1018 | 21.7977 | 22.5498 | 22.145 | 7.1331 | 9.0947 | 6.2154 | 6.905 | 7.0225 | 5.1615 | 0 | [14 empty] | 0.044254 |  | 50.8805 |  |  |  | 82.7129 |  | 38.6307 |  | 47.6787 |  | 49.3158 |  | 26.6411
03/29 04:00:00 | 22.1513 | 23.8461 | 22.6647 | 21.8919 | 21.581 | 22.3177 | 21.9385 | 5.9456 | 7.4202 | 5.1771 | 5.9787 | 6.0985 | 4.5268 | 0 | [14 empty] | 0.045267 |  | 35.3496 |  |  |  | 55.0587 |  | 26.8028 |  | 35.7453 |  | 37.1914 |  | 20.4923
03/29 05:00:00 | 22.0146 | 23.7357 | 22.5184 | 21.7523 | 21.4376 | 22.167 | 21.807 | 6.0636 | 7.5003 | 5.2172 | 6.078 | 6.2075 | 4.6562 | 0 | [14 empty] | 0.043101 |  | 36.7678 |  |  |  | 56.2542 |  | 27.219 |  | 36.9426 |  | 38.5327 |  | 21.6801
03/29 06:00:00 | 21.9202 | 23.6524 | 22.4183 | 21.6549 | 21.3376 | 22.0619 | 21.7063 | 5.9489 | 7.2798 | 5.1529 | 5.9672 | 6.0972 | 4.5946 | 0 | [14 empty] | 0.045761 |  | 35.3889 |  |  |  | 52.9948 |  | 26.5525 |  | 35.6081 |  | 37.1761 |  | 21.1101
03/29 07:00:00 | 21.8223 | 23.5641 | 22.3153 | 21.5532 | 21.2333 | 21.952 | 21.5372 | 5.8358 | 7.0684 | 5.061 | 5.852 | 5.9759 | 4.5247 | 0 | [14 empty] | 0.081276 |  | 34.056 |  |  |  | 49.9624 |  | 25.6135 |  | 34.2454 |  | 35.7113 |  | 20.4725
03/29 08:00:00 | 21.7394 | 23.485 | 22.2277 | 21.4649 | 21.1423 | 21.8552 | 21.3947 | 8.4288 | 10.3944 | 6.5542 | 8.7853 | 43.2178 | 7.6279 | 0 | [14 empty] | 0.11879 |  | 71.0441 |  |  |  | 108.0427 |  | 42.9579 |  | 77.1817 |  | 1867.78 |  | 58.1853
03/29 09:00:00 | 21.7668 | 23.5133 | 22.259 | 21.4827 | 21.3722 | 21.8591 | 21.4077 | 13.6318 | 9.1123 | 5.5975 | 17.4592 | 42.9692 | 14.7304 | 0 | [14 empty] | 0.12895 |  | 185.8252 |  |  |  | 83.0337 |  | 31.3316 |  | 304.8238 |  | 1846.3558 |  | 216.9836
03/29 10:00:00 | 22.0874 | 23.7178 | 22.5435 | 21.8139 | 23.4235 | 22.1635 | 21.6459 | 19.3349 | 7.2434 | 3.8396 | 28.5022 | 26.8556 | 21.686 | 0 | [14 empty] | 0.19499 |  | 373.8389 |  |  |  | 52.4672 |  | 14.7426 |  | 812.3763 |  | 721.2256 |  | 470.284
03/29 11:00:00 | 22.9828 | 24.4973 | 23.2187 | 22.9218 | 25.1881 | 23.2479 | 22.1159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.75147 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/29 12:00:00 | 23.713 | 25.4551 | 24.0533 | 23.9248 | 25.5911 | 24.3411 | 22.582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.2792 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/29 13:00:00 | 23.7332 | 25.6765 | 24.234 | 24.01 | 25.3639 | 24.5164 | 23.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.50852 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/29 14:00:00 | 23.8563 | 25.875 | 24.446 | 24.1593 | 25.3934 | 24.7421 | 23.4554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.16072 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/29 15:00:00 | 24.3689 | 26.4188 | 25.0243 | 24.6884 | 25.8317 | 25.3095 | 23.8277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.29288 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/29 16:00:00 | 24.8687 | 26.9464 | 25.5441 | 25.1928 | 26.2714 | 25.8268 | 24.0796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.62282 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/29 17:00:00 | 25.0932 | 27.2589 | 25.7792 | 25.433 | 26.4897 | 26.1264 | 24.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.41372 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/29 18:00:00 | 25.2214 | 27.4628 | 25.919 | 25.5696 | 26.6137 | 26.3257 | 24.6596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.31561 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/29 19:00:00 | 24.9956 | 27.2881 | 25.6909 | 25.3762 | 26.412 | 26.1144 | 24.5144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.23157 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/29 20:00:00 | 24.5855 | 26.7793 | 25.2028 | 24.9505 | 25.9741 | 25.6323 | 24.1394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.19901 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/29 21:00:00 | 24.1836 | 26.2958 | 24.7899 | 24.5954 | 25.5706 | 25.226 | 23.7585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.18073 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/29 22:00:00 | 23.7743 | 25.8669 | 24.4234 | 24.2441 | 25.1621 | 24.8663 | 23.3911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.14682 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/29 23:00:00 | 23.4535 | 25.4847 | 24.0734 | 23.9034 | 24.8195 | 24.5152 | 23.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.16031 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/29 24:00:00 | 23.2059 | 25.1512 | 23.8072 | 23.642 | 24.4781 | 24.1844 | 22.7357 | 16.6984 | 9.6254 | 5.4973 | 22.7344 | 30.0715 | 17.9409 | 0 | [14 empty] | 0.22113 |  | 278.8363 |  |  |  | 92.648 |  | 30.2202 |  | 516.8519 |  | 904.2955 |  | 321.8741
03/30 01:00:00 | 23.2686 | 24.9271 | 23.6099 | 23.7568 | 24.5697 | 24.1427 | 22.4449 | 12.0491 | 5.6585 | 3.9544 | 13.6194 | 18.8106 | 10.4315 | 0 | [14 empty] | 0.67839 |  | 145.1804 |  |  |  | 32.0191 |  | 15.6376 |  | 185.489 |  | 353.8371 |  | 108.8162
03/30 02:00:00 | 23.2214 | 24.6761 | 23.3295 | 23.7518 | 24.6765 | 24.0292 | 22.2226 | 11.6416 | 5.3494 | 3.7986 | 13.2853 | 17.449 | 10.2165 | 0 | [14 empty] | 0.99755 |  | 135.5263 |  |  |  | 28.6157 |  | 14.4291 |  | 176.4997 |  | 304.4676 |  | 104.3775
03/30 03:00:00 | 23.1349 | 24.4673 | 23.1221 | 23.6837 | 24.6821 | 23.8979 | 21.9727 | 11.3027 | 5.2959 | 3.781 | 12.9212 | 16.7624 | 10.0117 | 0 | [14 empty] | 1.3506 |  | 127.7518 |  |  |  | 28.047 |  | 14.2961 |  | 166.9563 |  | 280.9786 |  | 100.2338
03/30 04:00:00 | 23.035 | 24.2769 | 22.9341 | 23.5928 | 24.6319 | 23.7586 | 21.746 | 10.9755 | 5.2298 | 3.797 | 12.5218 | 16.1469 | 9.7682 | 0 | [14 empty] | 1.6614 |  | 120.4621 |  |  |  | 27.3503 |  | 14.4169 |  | 156.7954 |  | 260.7219 |  | 95.4187
03/30 05:00:00 | 22.9038 | 24.0657 | 22.7316 | 23.4638 | 24.5254 | 23.5899 | 21.533 | 10.6554 | 5.1877 | 3.8176 | 12.1041 | 15.4985 | 9.5179 | 0 | [14 empty] | 1.8793 |  | 113.5383 |  |  |  | 26.9126 |  | 14.574 |  | 146.5087 |  | 240.2037 |  | 90.5904
03/30 06:00:00 | 22.7493 | 23.8441 | 22.5186 | 23.2989 | 24.3755 | 23.4011 | 21.3332 | 8.8763 | 5.1527 | 3.8069 | 10.5435 | 15.0494 | 8.4711 | 0 | [14 empty] | 2.0053 |  | 78.7892 |  |  |  | 26.5499 |  | 14.4923 |  | 111.1652 |  | 226.4852 |  | 71.7597
03/30 07:00:00 | 22.6082 | 23.623 | 22.3082 | 23.1543 | 24.2022 | 23.2451 | 21.1503 | 8.3286 | 4.2047 | 3.1184 | 9.9723 | 12.6161 | 7.9124 | 0 | [14 empty] | 2.1254 |  | 69.3663 |  |  |  | 17.6794 |  | 9.7242 |  | 99.4478 |  | 159.1659 |  | 62.6054
03/30 08:00:00 | 22.5195 | 23.4717 | 22.1701 | 23.0625 | 24.0722 | 23.147 | 21.013 | 10.5677 | 5.9359 | 4.8406 | 12.6546 | 16.8821 | 9.6404 | 0 | [14 empty] | 2.2695 |  | 111.6756 |  |  |  | 35.2354 |  | 23.4316 |  | 160.1383 |  | 285.006 |  | 92.9364
03/30 09:00:00 | 22.5865 | 23.5064 | 22.2289 | 23.1237 | 24.1372 | 23.1933 | 20.9741 | 9.5725 | 5.1634 | 4.2742 | 11.4241 | 15.0993 | 8.5979 | 0 | [14 empty] | 2.5997 |  | 91.633 |  |  |  | 26.6608 |  | 18.2684 |  | 130.5104 |  | 227.9894 |  | 73.9246
03/30 10:00:00 | 22.8148 | 23.6904 | 22.5388 | 23.3349 | 24.3487 | 23.4018 | 21.0853 | 8.0075 | 4.1971 | 2.6956 | 9.6473 | 13.0254 | 6.9754 | 0 | [14 empty] | 2.9912 |  | 64.1198 |  |  |  | 17.6158 |  | 7.2661 |  | 93.0696 |  | 169.6622 |  | 48.6556
03/30 11:00:00 | 23.2599 | 24.1875 | 23.048 | 23.7703 | 24.766 | 23.906 | 21.2911 | 7.8303 | 3.852 | 2.8251 | 9.341 | 12.5847 | 6.8436 | 0 | [14 empty] | 3.8761 |  | 61.313 |  |  |  | 14.8376 |  | 7.9813 |  | 87.254 |  | 158.3737 |  | 46.8347
03/30 12:00:00 | 23.5856 | 24.5773 | 23.3963 | 24.0824 | 25.0508 | 24.262 | 21.2967 | 7.3032 | 3.6566 | 2.6264 | 8.7235 | 11.7226 | 6.3316 | 0 | [14 empty] | 5.2388 |  | 53.3361 |  |  |  | 13.371 |  | 6.898 |  | 76.0998 |  | 137.4202 |  | 40.0896
03/30 13:00:00 | 23.5363 | 24.5802 | 23.3602 | 24.0521 | 25.0284 | 24.2383 | 21.3254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.888 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/30 14:00:00 | 23.4818 | 24.5922 | 23.354 | 23.9985 | 24.9474 | 24.2081 | 21.3552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.5226 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/30 15:00:00 | 23.6314 | 24.8163 | 23.594 | 24.1256 | 25.0067 | 24.375 | 21.5341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 4.3987 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/30 16:00:00 | 23.7742 | 25.0728 | 23.8111 | 24.2466 | 25.0853 | 24.5649 | 21.8252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.7988 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/30 17:00:00 | 23.7978 | 25.1612 | 23.8799 | 24.2571 | 25.0708 | 24.6094 | 21.9287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.4934 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/30 18:00:00 | 23.7703 | 25.1691 | 23.8784 | 24.2186 | 25.0113 | 24.5925 | 22.0024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 3.1256 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/30 19:00:00 | 23.5612 | 24.9464 | 23.6345 | 23.9416 | 24.7152 | 24.3323 | 21.9662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2.5438 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/30 20:00:00 | 23.204 | 24.5408 | 23.2423 | 23.5295 | 24.2821 | 23.891 | 21.8931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.7185 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/30 21:00:00 | 22.8669 | 24.1869 | 22.9381 | 23.2111 | 23.9469 | 23.531 | 21.7723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.1983 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/30 22:00:00 | 22.599 | 23.9352 | 22.691 | 22.9488 | 23.6682 | 23.284 | 21.6104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.97724 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/30 23:00:00 | 22.3538 | 23.6934 | 22.4641 | 22.7054 | 23.4054 | 23.0524 | 21.4932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.74068 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/30 24:00:00 | 22.1214 | 23.4541 | 22.2463 | 22.4707 | 23.1506 | 22.8253 | 21.3677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.56815 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/31 01:00:00 | 21.9743 | 23.2493 | 22.1091 | 22.2778 | 22.9382 | 22.6361 | 21.2753 | 9.1671 | 7.2941 | 5.1398 | 12.2259 | 16.3739 | 10.1652 | 0 | [14 empty] | 0.48857 |  | 84.0352 |  |  |  | 53.2043 |  | 26.4177 |  | 149.4735 |  | 268.1058 |  | 103.3305
03/31 02:00:00 | 21.8447 | 23.0248 | 21.9197 | 22.1356 | 22.8255 | 22.4616 | 21.2306 | 6.5356 | 3.9884 | 3.2163 | 7.3617 | 9.4536 | 5.8839 | 0 | [14 empty] | 0.37708 |  | 42.7139 |  |  |  | 15.9072 |  | 10.3444 |  | 54.1946 |  | 89.3697 |  | 34.6208
03/31 03:00:00 | 21.7199 | 22.8305 | 21.7406 | 22.0313 | 22.7362 | 22.3229 | 21.22 | 5.4602 | 3.6019 | 2.6769 | 6.3543 | 8.0077 | 5.0922 | 0 | [14 empty] | 0.24987 |  | 29.8139 |  |  |  | 12.974 |  | 7.1658 |  | 40.3772 |  | 64.1225 |  | 25.931
03/31 04:00:00 | 21.6253 | 22.6664 | 21.6213 | 21.9449 | 22.6591 | 22.2177 | 21.1243 | 6.6819 | 3.6013 | 3.3009 | 7.3095 | 9.1499 | 5.8715 | 0 | [14 empty] | 0.25107 |  | 44.6474 |  |  |  | 12.9696 |  | 10.8956 |  | 53.4281 |  | 83.721 |  | 34.474
03/31 05:00:00 | 21.5294 | 22.5016 | 21.5021 | 21.8486 | 22.5641 | 22.1041 | 20.9607 | 5.4494 | 3.1303 | 2.7583 | 6.3001 | 7.807 | 5.129 | 0 | [14 empty] | 0.3234 |  | 29.6962 |  |  |  | 9.7985 |  | 7.608 |  | 39.6914 |  | 60.9487 |  | 26.3068
03/31 06:00:00 | 21.4199 | 22.3735 | 21.3756 | 21.7388 | 22.4535 | 21.9809 | 20.8263 | 5.3283 | 3.1917 | 2.7585 | 6.1238 | 7.6471 | 5.0384 | 0 | [14 empty] | 0.3524 |  | 28.3903 |  |  |  | 10.1868 |  | 7.6091 |  | 37.5006 |  | 58.4778 |  | 25.3857
03/31 07:00:00 | 21.3376 | 22.2827 | 21.2853 | 21.6512 | 22.3682 | 21.89 | 20.7112 | 5.0067 | 3.1167 | 2.6394 | 5.7782 | 7.2333 | 4.7492 | 0 | [14 empty] | 0.39237 |  | 25.0668 |  |  |  | 9.714 |  | 6.9665 |  | 33.3871 |  | 52.32 |  | 22.5552
03/31 08:00:00 | 21.2718 | 22.207 | 21.2143 | 21.5804 | 22.2937 | 21.8157 | 20.619 | 7.0692 | 4.3393 | 5.3256 | 7.387 | 9.2751 | 5.8694 | 0 | [14 empty] | 0.42617 |  | 49.9741 |  |  |  | 18.8295 |  | 28.362 |  | 54.5682 |  | 86.028 |  | 34.4495
03/31 09:00:00 | 21.3204 | 22.2199 | 21.2623 | 21.6142 | 22.3185 | 21.8424 | 20.5572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.5825 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/31 10:00:00 | 21.4786 | 22.3673 | 21.4633 | 21.7703 | 22.4415 | 22.0001 | 20.5572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0.84899 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/31 11:00:00 | 21.6657 | 22.5765 | 21.7031 | 21.9497 | 22.5565 | 22.1932 | 20.6677 | 0 | 0 | 0 | 0 | 0 | 0 | 53.3744 | [14 empty] | 0.99593 |  | 2848.8264 |  |  |  | 2848.8264 |  | 2848.8264 |  | 2848.8264 |  | 2848.8264 |  | 2848.8264
03/31 12:00:00 | 21.7827 | 22.7179 | 21.8556 | 22.0565 | 22.6175 | 22.3132 | 21.9728 | 0 | 0 | 0 | 0 | 0 | 0 | 26.9986 | [14 empty] | 0.036139 |  | 728.9219 |  |  |  | 728.9219 |  | 728.9219 |  | 728.9219 |  | 728.9219 |  | 728.9219
03/31 13:00:00 | 21.6273 | 22.6061 | 21.7175 | 21.8886 | 22.4395 | 22.1616 | 22.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9154 | [14 empty] | 0.73551 |  | 79.4847 |  |  |  | 79.4847 |  | 79.4847 |  | 79.4847 |  | 79.4847 |  | 79.4847
03/31 14:00:00 | 21.5655 | 22.5773 | 21.6798 | 21.8115 | 22.3466 | 22.1024 | 22.4535 | 0 | 0 | 0 | 0 | 0 | 0 | 13.3574 | [14 empty] | 0.78863 |  | 178.4209 |  |  |  | 178.4209 |  | 178.4209 |  | 178.4209 |  | 178.4209 |  | 178.4209
03/31 15:00:00 | 21.7603 | 22.7947 | 21.9196 | 21.992 | 22.5061 | 22.2952 | 22.426 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3458 | [14 empty] | 0.44322 |  | 1.8111 |  |  |  | 1.8111 |  | 1.8111 |  | 1.8111 |  | 1.8111 |  | 1.8111
03/31 16:00:00 | 21.893 | 22.952 | 22.0825 | 22.1134 | 22.6104 | 22.4295 | 22.2506 | 0 | 0 | 0 | 0 | 0 | 0 | 11.6956 | [14 empty] | 0.12785 |  | 136.788 |  |  |  | 136.788 |  | 136.788 |  | 136.788 |  | 136.788 |  | 136.788
03/31 17:00:00 | 21.8301 | 22.9153 | 22.0264 | 22.042 | 22.5287 | 22.3678 | 22.2316 | 0 | 0 | 0 | 0 | 0 | 0 | 15.8427 | [14 empty] | 0.16116 |  | 250.9924 |  |  |  | 250.9924 |  | 250.9924 |  | 250.9924 |  | 250.9924 |  | 250.9924
03/31 18:00:00 | 21.6966 | 22.8352 | 21.899 | 21.8983 | 22.3712 | 22.2335 | 22.3013 | 0 | 0 | 0 | 0 | 0 | 0 | 13.8436 | [14 empty] | 0.36571 |  | 191.644 |  |  |  | 191.644 |  | 191.644 |  | 191.644 |  | 191.644 |  | 191.644
03/31 19:00:00 | 21.4123 | 22.6115 | 21.5528 | 21.6047 | 22.0662 | 21.9459 | 22.3221 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2246 | [14 empty] | 0.82774 |  | 17.8476 |  |  |  | 17.8476 |  | 17.8476 |  | 17.8476 |  | 17.8476 |  | 17.8476
03/31 20:00:00 | 21.1165 | 22.3209 | 21.2193 | 21.301 | 21.7536 | 21.6451 | 22.1836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.1389 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/31 21:00:00 | 20.9143 | 22.0482 | 21.018 | 21.0934 | 21.4803 | 21.4382 | 21.9913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.1598 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/31 22:00:00 | 20.7862 | 21.8537 | 20.8961 | 20.9608 | 21.2933 | 21.3051 | 21.8311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 1.0919 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
03/31 23:00:00 | 20.5892 | 21.6525 | 20.7059 | 20.7554 | 21.0952 | 21.0984 | 21.6395 | 8.714 | 6.104 | 7.8421 | 10.468 | 12.5326 | 9.3231 | 0 | [14 empty] | 1.1031 |  | 75.9341 |  |  |  | 37.2593 |  | 61.4982 |  | 109.5785 |  | 157.0671 |  | 86.9193
03/31 24:00:00 | 20.4524 | 21.4734 | 20.564 | 20.6076 | 20.9626 | 20.9354 | 21.4413 | 8.4262 | 4.1041 | 6.8352 | 7.9649 | 8.8406 | 6.9009 | 1.8322 | [14 empty] | 0.97792 |  | 43.4807 |  |  |  | 5.1615 |  | 25.0296 |  | 37.6097 |  | 49.1181 |  | 25.6921